## JWPN TCL LAMPU (hidden)
BLOK PENTADBIRAN DAN AKTIVITI
PELAN SILING LANTAI BAWAH
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Lamp type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | Bilik Seminar 3 | Rhea Low Bright 2x 36 Flouresent Lamp | 4 | 84 | 336 | 0.8 | 268.8 | 1120 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 | 33.3333 |  |  | 6 | 1.5mm
1.5mm
Y1 | Bilik Seminar 4 | Rhea Low Bright 2x 36 Flouresent Lamp | 4 | 84 | 336 | 0.8 | 268.8 |  | 1120 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
B1 | Bilik Seminar 6 | Rhea Low Bright 2x 36 Flouresent Lamp | 4 | 84 | 336 | 0.8 | 268.8 |  |  | 1120 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
R2 | Bilik Seminar 2 | Rhea Low Bright 2x 36 Flouresent Lamp | 4 | 84 | 336 | 0.8 | 268.8 | 1120 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 | 33.3333 |  |  | 6 | 1.5mm
Y2 | Bilik Seminar 5 | Rhea Low Bright 2x 36 Flouresent Lamp | 4 | 84 | 336 | 0.8 | 268.8 |  | 1120 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
B2 | Bilik Seminar 1 | Rhea Low Bright 2x 36 Flouresent Lamp | 6 | 84 | 504 | 0.8 | 403.2 |  |  | 1680 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
R3 | Bilik Rehat | Rhea Low Bright 2x 36 Flouresent Lamp | 3 | 84 | 252 | 0.8 | 201.6 | 840 |  |  | 6 | 1.5mm
| Minuman Ringan | Rhea Low Bright 2x 36 Flouresent Lamp | 3 | 84 | 252 | 0.8 | 201.6 | 840 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 | 66.6667 |  |  | 6 | 1.5mm
Y3 | Coridor 1 | Project Batern 1x 36 Flouresent Lamp | 2 | 42 | 84 | 0.8 | 67.2 |  | 280 |  | 6 | 1.5mm
| Coridor 2 | Project batern 1x 36 Flouresent Lamp | 3 | 42 | 126 | 0.8 | 100.8 |  | 420 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 |  | 66.6667 |  | 6 | 1.5mm
B3 | Tandas Lelaki | Rhea Low Bright 3x 18 Flouresent Lamp | 2 | 72 | 144 | 0.8 | 115.2 |  |  | 480 | 6 | 1.5mm
| Tandas Kakitangan Lelaki | Rhea Low Bright 3x 18 Flouresent Lamp | 1 | 72 | 72 | 0.8 | 57.6 |  |  | 240 | 6 | 1.5mm
| Tandas Orang Cacat | Rhea Low Bright 3x 18 Flouresent Lamp | 1 | 72 | 72 | 0.8 | 57.6 |  |  | 240 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 3 | 10 | 30 | 0.8 | 24 |  |  | 100 | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 3 | 20 | 60 | 0.8 | 48 |  |  | 200 | 6 | 1.5mm
| Exhaust Fan | Exhaust fan | 1 | 70 | 70 | 0.8 | 56 |  |  | 233.3333 | 6 | 1.5mm
R4 | Stor | Rhea Low Bright 3x 18 Flouresent Lamp | 2 | 72 | 144 | 0.8 | 115.2 | 480 |  |  | 6 | 1.5mm
| Bilik Keyphone | Rhea Low Bright 3x 18 Flouresent Lamp | 4 | 72 | 288 | 0.8 | 230.4 | 960 |  |  | 6 | 1.5mm
| Pantry | Rhea Low Bright 3x 18 Flouresent Lamp | 1 | 72 | 72 | 0.8 | 57.6 | 240 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 3 | 10 | 30 | 0.8 | 24 | 100 |  |  | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 2 | 20 | 40 | 0.8 | 32 | 133.3333 |  |  | 6 | 1.5mm
Y4 | Pejabat PBSD | Rhea Low Bright 3x 18 Flouresent Lamp | 10 | 72 | 720 | 0.8 | 576 |  | 2400 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 |  | 66.6667 |  | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 1 | 20 | 20 | 0.8 | 16 |  | 66.6667 |  | 6 | 1.5mm
B4 | Pejabat PBSD | Rhea Low Bright 3x 18 Flouresent Lamp | 10 | 72 | 720 | 0.8 | 576 |  |  | 2400 | 6 | 1.5mm
R5 | Pejabat PBSD | Rhea Low Bright 3x 18 Flouresent Lamp | 10 | 72 | 720 | 0.8 | 576 | 2400 |  |  | 6 | 1.5mm
Y5 | Pejabat PBSD | Rhea Low Bright 3x 18 Flouresent Lamp | 10 | 72 | 720 | 0.8 | 576 |  | 2400 |  | 6 | 1.5mm
B5 | Bilik Mesyuarat | Rhea Low Bright 3x 18 Flouresent Lamp | 6 | 72 | 432 | 0.8 | 345.6 |  |  | 1440 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 1 | 20 | 20 | 0.8 | 16 |  |  | 66.6667 | 6 | 1.5mm
R6 | Bilik Mesyuarat | Rhea Low Bright 3x 18 Flouresent Lamp | 6 | 72 | 432 | 0.8 | 345.6 | 1440 |  |  | 6 | 1.5mm
Y6 | Pejabat NGO | Rhea Low Bright 3x 18 Flouresent Lamp | 9 | 72 | 648 | 0.8 | 518.4 |  | 2160 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 1 | 20 | 20 | 0.8 | 16 |  | 66.6667 |  | 6 | 1.5mm
B6 | Pejabat NGO | Rhea Low Bright 3x 18 Flouresent Lamp | 8 | 72 | 576 | 0.8 | 460.8 |  |  | 1920 | 6 | 1.5mm
R7 | Pejabat NGO | Rhea Low Bright 3x 18 Flouresent Lamp | 8 | 72 | 576 | 0.8 | 460.8 | 1920 |  |  | 6 | 1.5mm
Y7 | Bilik Kuliah 6 | Rhea Low Bright 2x 36 Flouresent Lamp | 8 | 84 | 672 | 0.8 | 537.6 |  | 2240 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
B7 | Bilik Kuliah 7 | Rhea Low Bright 2x 36 Flouresent Lamp | 8 | 84 | 672 | 0.8 | 537.6 |  |  | 2240 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
R8 | Bilik Kuliah 8 | Rhea Low Bright 2x 36 Flouresent Lamp | 8 | 84 | 672 | 0.8 | 537.6 | 2240 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 | 33.3333 |  |  | 6 | 1.5mm
Y8 | Bilik Kuliah 9 | Rhea Low Bright 2x 36 Flouresent Lamp | 8 | 84 | 672 | 0.8 | 537.6 |  | 2240 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
B8 | Coridor 3 | Project Batern 1x36 Flouresent Lamp | 3 | 42 | 126 | 0.8 | 100.8 |  |  | 420 | 6 | 1.5mm
| Coridor 4 | Project Batern 1x36 Flouresent Lamp | 3 | 42 | 126 | 0.8 | 100.8 |  |  | 420 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 |  |  | 66.6667 | 6 | 1.5mm
R9 | Stor NGO | Rhea Low Bright 3x 18 Flouresent Lamp | 6 | 72 | 432 | 0.8 | 345.6 | 1440 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 | 33.3333 |  |  | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 1 | 20 | 20 | 0.8 | 16 | 66.6667 |  |  | 6 | 1.5mm
Y9 | Tandas wanita | Rhea Low Bright 3x 18 Flouresent Lamp | 4 | 72 | 288 | 0.8 | 230.4 |  | 960 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 |  | 66.6667 |  | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 2 | 20 | 40 | 0.8 | 32 |  | 133.3333 |  | 6 | 1.5mm
| Exhaust Fan | Exhaust fan | 1 | 70 | 70 | 0.8 | 56 |  | 233.3333 |  | 6 | 1.5mm
B9 | Ruang Legar 1 | 1 x 18 W Sheratan Compact Flouresent Downlight | 8 | 24 | 192 | 0.8 | 153.6 |  |  | 640 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 |  |  | 66.6667 | 6 | 1.5mm
R10 | Ruang Legar 1 | 1 x 18 W Sheratan Compact Flouresent Downlight | 8 | 24 | 192 | 0.8 | 153.6 | 640 |  |  | 6 | 1.5mm
Y10 | Ruang Legar 2 | 1 x 18 W Sheratan Compact Flouresent Downlight | 4 | 24 | 96 | 0.8 | 76.8 |  | 320 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
B10 | Ruang Legar 3 | 1 x 18 W Sheratan Compact Flouresent Downlight | 4 | 24 | 96 | 0.8 | 76.8 |  |  | 320 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
R11 | Tangga 1 | Project Batern 1x36 Flouresent Lamp | 1 | 42 | 42 | 0.8 | 33.6 | 140 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 | 33.3333 |  |  | 6 | 1.5mm
B11 | Tangga 2 | Project Batern 1x36 Flouresent Lamp | 1 | 42 | 42 | 0.8 | 33.6 |  |  | 140 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
Y11
|  |  | 247 | 3110 | 14264 |  | 11411.2 | 16353.3333 | 16560 | 14633.3333

## JWPN TCL SOKET (hidden)
BLOK PENTADBIRAN DAN AKTIVITI
PELAN SILING LANTAI BAWAH
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Socket type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | Bilik Rehat | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
| Bilik Seminar 3 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
Y1 | Bilik Seminar 1 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  | 416.6667 |  | 20 | 2.5mm
| Bilik Seminar 2 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  | 416.6667 |  | 20 | 2.5mm
B1 | Minuman Ringan | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R2 | Bilik Seminar 5 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
| Ruang Legar 1 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
Y2 | Bilik Kuliah 6 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  | 416.6667 |  | 20 | 2.5mm
| Bilik Kuliah 8 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  | 416.6667 |  | 20 | 2.5mm
B2 | Bilik Kuliah 7 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  |  | 416.6667 | 20 | 2.5mm
R3 | Coridor 4 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
| Stor NGO | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
Y3 | Bilik Keyphone | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B3 | Bilik Keyphone | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  |  | 416.6667 | 20 | 2.5mm
R4 | Stor | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
| Pantry | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
Y4 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B4 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R5 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y5 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B5 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R6 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y6 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B6 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R7 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y7 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B7 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R8 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y8 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B8 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R9 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y9 | Bilik Mesyuarat | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B9 | Bilik Mesyuarat | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R10 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y10 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B10 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R11 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y11 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B11 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R12 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y12 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B12 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
TOTAL |  |  | 70 | 10500 | 17500 |  | 7000 | 10000 | 10000 | 9166.6667

## HEPA 2ND FLOOR -TCL SOKET KOSO
HEPA LEVEL 2
TCL SOCKET
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Socket type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
(RING) R1 | PEJABAT AM | 13A S/S/0 | 10 | 250 | 2500 | 0.4 | 1000 | 5115.0895 | 5115.0895 | 5115.0895 | 32 | 2.5mm
(RING) Y1 | LA L U A N WING AB | 13A S/S/0 | 8 | 250 | 2000 | 0.4 | 800 |  | 4092.0716 |  | 32 | 2.5mm
(RING) B1 | BILIK PEGAWAI 3 | 13A S/S/0 | 7 | 250 | 1750 | 0.4 | 700 | 3580.5627 |  | 3580.5627 | 32 | 2.5mm
(RING) R2 | RUANG KERJA 20 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  | 32 | 2.5mm
| RUANG KERJA 21 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  |  | 2.5mm
Y2 | BILIK ALAT TULIS | 13A S/S/0 | 3 | 250 | 750 | 0.4 | 300 |  | 1534.5269 |  | 32 | 4mm
| RISER ICT | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 1023.0179 |  |  | 4mm
(RING) B2 | RUANG KERJA 16 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 |  |  | 2046.0358 | 32 | 2.5mm
| RUANG KERJA 17 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 |  |  | 2046.0358 |  | 2.5mm
(RING) R3 | RUANG KERJA 18 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  | 32 | 2.5mm
| RUANG KERJA 19 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  |  | 2.5mm
(RING) Y3 | LALUAN | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  | 511.509 |  | 32
| PANTRI | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 1023.0179 |  |  | 2.5mm
| BILIK RANGKAIAN ICT | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 |  | 2046.0358 |  |  | 2.5mm
B3 | BILIK SWITCH BOARD(ROOF) | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  |  | 511.509 | 32 | 4mm
| LALUAN | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  |  | 511.509 |  | 4mm
| TANDAS(P)(L) | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 1023.0179 |  | 4mm
R4 | RUANG MENUNGGU | 13A S/S/0 | 5 | 250 | 1250 | 0.4 | 500 | 2557.5448 |  |  | 32 | 4mm
| LALUAN | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 511.509 |  |  |  | 4mm
(RING) Y4 | RUANG KERJA 12 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 |  | 2046.0358 |  | 32 | 2.5mm
| RUANG KERJA 13 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 |  | 2046.0358 |  |  | 2.5mm
(RING) B4 | BILIK SUIS | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 1023.0179 | 32 | 2.5mm
| BILIK PEGAWAI 2 | 13A S/S/0 | 6 | 250 | 1500 | 0.4 | 600 |  |  | 3069.0537 |  | 2.5mm
R5 | LALUAN | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 1023.0179 |  |  | 32 | 4mm
| RUANG KERJA 14 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  |  | 4mm
(RING) Y5 | BILIK PEGAWAI 1 (p1) | 13A S/S/0 | 10 | 250 | 2500 | 0.4 | 1000 |  | 5115.0895 |  | 32 | 2.5mm
(RING) B5 | BILIK E.L.V | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 1023.0179 | 32 | 2.5mm
| BILIK MESYUARAT UTAMA (p1) | 13A S/S/0 | 7 | 250 | 1750 | 0.4 | 700 |  |  | 3580.5627 |  | 2.5mm
R6 | RUANG KERJA 15 | 13A S/S/0 | 3 | 250 | 750 | 0.4 | 300 | 1534.5269 |  |  | 32 | 4mm
Y6 | BILIK PEGAWAI 1 (p2) | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 1023.0179 |  | 20 | 2.5mm
B6 | BILIK MESYUARAT UTAMA (p2) | 13A S/S/0 | 6 | 250 | 1500 | 0.4 | 600 |  |  | 3069.0537 | 32 | 4mm
TOTAL |  |  | 123 |  | 30750 |  | 12300 | 24552.4297 | 25575.4476 | 26598.4655
3

## HEPA 2ND FLOOR-TCL LAMBU & FAN
HEPA LEVEL2
TCL LAMB Calculation
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Lamp type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | TANGGA 2 | FLUORESCENT 1X36W+BALLAST 6W | 3 | 42 | 126 | 0.8 | 100.8 | 515.601 |  |  | 6 | 1.5mm
| PEJABAT AM P1 | FLUORESCENT 2X36W+BALLAST 6W | 7 | 84 | 588 | 0.8 | 470.4 | 2406.1381 |  |  |  | 1.5mm
Y1 | PEJABAT AM P2 | FLUORESCENT 2X36W+BALLAST 6W | 1 | 84 | 84 | 0.8 | 67.2 |  | 343.734
| L A L U A N 2.1 | FLUORESCENT 1X36W+BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 |  | 343.734 |  | 6 | 1.5mm
| L A L U A N 2.2 | FLUORESCENT 1X36W+BALLAST 6W | 4 | 42 | 168 | 0.8 | 134.4 |  | 687.468 |  |  | 1.5mm
B1 | L A L U A N 2.3 | FLUORESCENT 1X36W+BALLAST 6W | 6 | 42 | 252 | 0.8 | 201.6 |  |  | 1031.202 | 6 | 1.5mm
| L A L U A N 2.4 | FLUORESCENT 1X36W+BALLAST 6W | 4 | 42 | 168 | 0.8 | 134.4 |  |  | 687.468 |  | 1.5mm
R2 | BILIK PEGAWAI 3 | FLUORESCENT 2X36W+BALLAST 6W | 5 | 84 | 420 | 0.8 | 336 | 1718.6701 |  |  | 6 | 1.5mm
| RUANG KERJA 20 | FLUORESCENT 2X36W+BALLAST 6W | 3 | 84 | 252 | 0.8 | 201.6 | 1031.202 |  |  |  | 1.5mm
Y2 | RUANG KERJA 21 | FLUORESCENT 2X36W+BALLAST 6W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  | 6 | 1.5mm
| BILIK ALAT TULIS | FLUORESCENT 2X36W+BALLAST 6W | 2 | 84 | 168 | 0.8 | 134.4 |  | 687.468 |  |  | 1.5mm
| RISER ICT | FLUORESCENT 2X36W+BALLAST 6W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  |  | 1.5mm
| ELEKTRIK | FLUORESCENT 1X18W+BALLAST 6W | 1 | 24 | 24 | 0.8 | 19.2 |  | 98.2097 |  |  | 1.5mm
B2 | RUANG KERJA 16 | FLUORESCENT 2X36W+BALLAST 6W | 5 | 84 | 420 | 0.8 | 336 |  |  | 1718.6701 | 6 | 1.5mm
| RUANG KERJA 17 | FLUORESCENT 2X36W+BALLAST 6W | 3 | 84 | 252 | 0.8 | 201.6 |  |  | 1031.202 |  | 1.5mm
R3 | RUANG KERJA 18 | FLUORESCENT 2X36W+BALLAST 6W | 3 | 84 | 252 | 0.8 | 201.6 | 1031.202 |  |  | 6 | 1.5mm
| RUANG KERJA 19 | FLUORESCENT 2X36W+BALLAST 6W | 4 | 84 | 336 | 0.8 | 268.8 | 1374.9361 |  |  |  | 1.5mm
Y3 | TANGGA 1 | FLUORESCENT 1X36W+BALLAST 6W | 3 | 42 | 126 | 0.8 | 100.8 |  | 515.601 |  | 6 | 1.5mm
| L A L U A N 2.5 | FLUORESCENT 1X36W+BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 |  | 171.867 |  |  | 1.5mm
| BILIK RANGKAIAN ICT | FLUORESCENT 2X36W+BALLAST 6W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  |  | 1.5mm
| PANTRI | FLUORESCENT 2X36W+BALLAST 6W | 2 | 84 | 168 | 0.8 | 134.4 |  | 687.468 |  |  | 1.5mm
| SALUR A/C | FLUORESCENT 1X18W+BALLAST 6W | 1 | 24 | 24 | 0.8 | 19.2 |  | 98.2097 |  |  | 1.5mm
B3 | TANDAS(P)(L)+SERVIS | FLUORESCENT 1X36W+BALLAST 6W | 8 | 42 | 336 | 0.8 | 268.8 |  |  | 1374.9361 | 6 | 1.5mm
| L A L U A N 2.7 | FLUORESCENT 1X36W+BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 |  |  | 343.734 |  | 1.5mm
R4 | L A L U A N 2.6 | FLUORESCENT 1X36W+BALLAST 6W | 4 | 42 | 168 | 0.8 | 134.4 | 687.468 |  |  | 6 | 1.5mm
| TANGGA 3 | FLUORESCENT 1X36W+BALLAST 6W | 3 | 42 | 126 | 0.8 | 100.8 | 515.601 |  |  |  | 1.5mm
| L A L U A N 2.8 | FLUORESCENT 1X36W+BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 | 343.734 |  |  |  | 1.5mm
Y4 | BILIK E.L.V | FLUORESCENT 1X18W+BALLAST 6W | 1 | 24 | 24 | 0.8 | 19.2 |  | 98.2097 |  | 6 | 1.5mm
| H/R | FLUORESCENT 1X18W+BALLAST 6W | 1 | 24 | 24 | 0.8 | 19.2 |  | 98.2097 |  |  | 1.5mm
| L A L U A N 2.1.2 | FLUORESCENT 1X36W+BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 |  | 343.734 |  |  | 1.5mm
| L A L U A N 2.1.3 | FLUORESCENT 1X36W+BALLAST 6W | 6 | 42 | 252 | 0.8 | 201.6 |  | 1031.202 |  |  | 1.5mm
B4 | L A L U A N 2.1.1 | FLUORESCENT 1X36W+BALLAST 6W | 4 | 42 | 168 | 0.8 | 134.4 |  |  | 687.468 | 6 | 1.5mm
| LALUAN 2.9 | FLUORESCENT 1X36W+BALLAST 6W | 4 | 42 | 168 | 0.8 | 134.4 |  |  | 687.468 |  | 1.5mm
R5 | RUANG MENUNGGU | FLUORESCENT 1X36W+BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 | 343.734 |  |  | 6 | 1.5mm
| RUANG KERJA 13 | FLUORESCENT 2X36W+BALLAST 6W | 3 | 84 | 252 | 0.8 | 201.6 | 1031.202 |  |  |  | 1.5mm
| BILIK PEGAWAI 2 | FLUORESCENT 2X36W+BALLAST 6W | 5 | 84 | 420 | 0.8 | 336 | 1718.6701 |  |  |  | 1.5mm
Y5 | BILIK PEGAWAI 1 | FLUORESCENT 2X36W+BALLAST 6W | 7 | 84 | 588 | 0.8 | 470.4 |  | 2406.1381 |  | 6 | 1.5mm
| RUANG KERJA 14 | FLUORESCENT 2X36W+BALLAST 6W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  |  | 1.5mm
B5 | BILIK MESYUARAT UTAMA | FLUORESCENT 2X36W+BALLAST 6W | 10 | 84 | 840 | 0.8 | 672 |  |  | 3437.3402 | 6 | 1.5mm
R6 | RUANG KERJA 12 | FLUORESCENT 2X36W+BALLAST 6W | 3 | 84 | 252 | 0.8 | 201.6 | 1031.202 |  |  | 6 | 1.5mm
| EMERGICY LIGHT | CEILING MOUNTED 1X1.2W | 7 | 1.2 | 8.4 | 0.8 | 6.72 | 34.3734 |  |  |  | 1.5mm
Y6 | EMERGICY LIGHT | CEILING MOUNTED 1X1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 |  | 49.1049 |  | 6 | 1.5mm
B6 | EMERGICY LIGHT | CEILING MOUNTED 1X1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 |  |  | 49.1049 | 6 | 1.5mm
R7 | EMERGICY LIGHT | CEILING MOUNTED 1X1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 | 49.1049 |  |  | 6 | 1.5mm
Y7 | EMERGICY LIGHT | CEILING MOUNTED 1X1.2W | 1 | 1.2 | 1.2 | 0.8 | 0.96 |  | 4.9105 |  | 6 | 1.5mm
| EXIT SIGN CEILING | KELUAR' SIGN 1X2.5W | 9 | 2.5 | 22.5 | 0.8 | 18 |  | 92.0716 |  |  | 1.5mm
B7 | EXIT SIGN CEILING | KELUAR' SIGN 1X2.5W | 5 | 2.5 | 12.5 | 0.8 | 10 |  |  | 51.1509 | 6 | 1.5mm
| EXIT SIGN WALL | KELUAR' SIGN 1X2.5W | 5 | 2.5 | 12.5 | 0.8 | 10 |  |  | 51.1509 |  | 1.5mm
R8 | EXIT SIGN WALL | KELUAR' SIGN 1X2.5W | 10 | 2.5 | 25 | 0.8 | 20 | 102.3018 |  |  | 6 | 1.5mm
Y8 | EXIT SIGN WALL | KELUAR' SIGN 1X2.5W | 5 | 2.5 | 12.5 | 0.8 | 10 |  | 51.1509 |  | 6 | 1.5mm
| EXUSTE FAN | VENTILATING FANS 1X25.7W | 2 | 25.7 | 51.4 | 0.8 | 41.12 |  | 210.3325 |  |  | 1.5mm
| CEILING FAN | REGULATOR FANS 1 X54W | 1 | 54 | 54 | 0.8 | 43.2 |  | 220.9719 |  |  | 1.5mm
TOTAL |  |  | 214 | 2504.2 | 9152 |  | 7321.6 | 13935.1407 | 12364.6036 | 11150.8951

## HEPA 2ND FLOOR-AC
HEPA LEVEL 2
Air-Condition Calculation
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | AC Power Unit [HP] |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | PEJABAT AM (1) | 1.5 | 1 | 850 | 850 | 1 | 850 | 4347.8261 |  |  | 32 | 4mm
Y1 | BILIK PEGAWAI 3 | 2.5 | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4mm
B1 | RUANG KERJA 20 | 1 | 1 | 850 | 850 | 1 | 850 |  |  | 4347.8261 | 32 | 4mm
R2 | RUANG KERJA 21 | 1 | 1 | 850 | 850 | 1 | 850 | 4347.8261 |  |  | 32 | 4mm
Y2 | BILIK ALAT TULIS | 1 | 1 | 850 | 850 | 1 | 850 |  | 4347.8261 |  | 32 | 4mm
B2 | RISER ICT | 1 | 1 | 850 | 850 | 1 | 850 |  |  | 4347.8261 | 32 | 4mm
R3 | RUANG KERJA 16 | 2 | 1 | 1730 | 1730 | 1 | 1730 | 8849.1049 |  |  | 32 | 4mm
Y3 | RUANG KERJA 17 | 1 | 1 | 850 | 850 | 1 | 850 |  | 4347.8261 |  | 32 | 4mm
B3 | RUANG KERJA 18 | 1 | 1 | 850 | 850 | 1 | 850 |  |  | 4347.8261 | 32 | 4mm
R4 | RUANG KERJA 19 | 1.5 | 1 | 1090 | 1090 | 1 | 1090 | 5575.4476 |  |  | 32 | 4mm
Y4 | BILIK RANGKAIAN ICT | 1.5 | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4mm
B4 | RUANG MENUNGGU | 1.5 | 1 | 1090 | 1090 | 1 | 1090 |  |  | 5575.4476 | 32 | 4mm
R5 | RUANG KERJA 12 | 1 | 1 | 850 | 850 | 1 | 850 | 4347.8261 |  |  | 32 | 4mm
Y5 | RUANG KERJA 13 | 1 | 1 | 850 | 850 | 1 | 850 |  | 4347.8261 |  | 32 | 4mm
B5 | RUANG KERJA 15 | 1 | 1 | 850 | 850 | 1 | 850 |  |  | 4347.8261 | 32 | 4mm
R6 | BILIK MESYUARAT UTAMA (1) | 2.5 | 1 | 2186 | 2186 | 1 | 2186 | 11181.5857 |  |  | 32 | 4mm
Y6 | BILIK PEGAWAI 1 (1) | 2 | 1 | 1730 | 1730 | 1 | 1730 |  | 8849.1049 |  | 32 | 4mm
B6 | BILIK PEGAWAI 1 (2) | 2 | 1 | 1730 | 1730 | 1 | 1730 |  |  | 8849.1049 | 32 | 4mm
R7 | BILIK PEGAWAI 2 | 2.5 | 1 | 2186 | 2186 | 1 | 2186 | 11181.5857 |  |  | 32 | 4mm
Y7 | BILIK MESYUARAT UTAMA (2) | 2.5 | 1 | 2186 | 2186 | 1 | 2186 |  | 11181.5857 |  | 32 | 4mm
B7 | BILIK MESYUARAT UTAMA (3) | 2.5 | 1 | 2186 | 2186 | 1 | 2186 |  |  | 11181.5857 | 32 | 4mm
R8 | RUANG KERJA 14 | 1 | 1 | 850 | 850 | 1 | 850 | 4347.8261 |  |  | 32 | 4mm
Y8 | PEJABAT AM (2) | 1.5 | 1 | 1730 | 1730 | 1 | 1730 |  | 8849.1049 |  | 32 | 4mm
B8 | PEJABAT AM (3) | 1.5 | 1 | 1730 | 1730 | 1 | 1730 |  |  | 8849.1049 | 32 | 4mm
TOTAL |  |  | 24 | 31104 | 31104 |  | 31104 | 54179.0281 | 53074.1688 | 51846.5473

## MSB & SSB
HEPA BUILDING
HEPA FLOOR 1 | TCL (W) | MD (W)
DB (LIGHT&FAN) | 12865.2 | 10292.16
DB (AC) | 44576 | 44576
DB (POWER) | 32750 | 13100 | CURENT SSB
SSB | 90191.2 | 67968.16 | 150.0408
HEPA FLOOR 2 & ROOF | TCL (W) | MD (W)
DB (LIGHT&FAN) | 9152 | 7321.6
DB (POWER) | 30750 | 12300
DB (AC) | 31104 | 31104 | CURENT SSB
SSB | 71006 | 50725.6 | 111.9776
MSB | TCL (W) | MD (W)
HEPA | 161197.2 | 118693.76

## HEPA 2ND FLOOR-AC CALCULATION
No | Room | Area (m²) | Heat Factor | Area (ft²) | Calculated HP | Final AC Selection | Qty AC | Remarks
1 | PEJABAT AM | 54 | 70 | 581.256 | 4.2829 | 1.5 | 3
2 | BILIK PEGAWAI 3 | 27 | 70 | 290.628 | 2.1415 | 2.5 | 1
3 | RUANG KERJA 20 | 13.65 | 60 | 146.9286 | 0.92797 | 1 | 1
4 | RUANG KERJA 21 | 13.65 | 60 | 146.9286 | 0.92797 | 1 | 1
5 | BILIK ALAT TULIS | 6.528 | 70 | 70.2674 | - | 1 | 1
6 | RISER ICT | 13.5 | 60 | 145.314 | 0.91777 | 1 | 1
7 | RUANG KERJA 16 | 27 | 60 | 290.628 | 1.8355 | 2 | 1
8 | RUANG KERJA 17 | 13.5 | 60 | 145.314 | 0.91777 | 1 | 1
9 | RUANG KERJA 18 | 13.5 | 60 | 145.314 | 0.91777 | 1 | 1
10 | RUANG KERJA 19 | 20.025 | 60 | 215.5491 | 1.3614 | 1.5 | 1
11 | BILIK RANGKAIAN ICT | 15.4 | 60 | 165.7656 | 1.0469 | 1.5 | 1
12 | PANTRI | 10 | 60 | 107.64 | - | CEILING FAN | 1 | No AC required
13 | TANDAS(P)(L) | 30 | 60 | 322.92 | - | EXUAST FAN | 1 | No AC required
14 | RUANG MENUNGGU | 17.08 | 70 | 183.8491 | 1.3547 | 1.5 | 1
15 | RUANG KERJA 12 | 13.95 | 60 | 150.1578 | 0.94837 | 1 | 1
16 | RUANG KERJA 13 | 13.95 | 60 | 150.1578 | 0.94837 | 1 | 1
17 | RUANG KERJA 14 | 13.635 | 60 | 146.7671 | 0.92695 | 1 | 1
| RUANG KERJA 15 | 10 | 60 | 107.64 | 0.67983 | 1
18 | BILIK PEGAWAI 1 | 40.05 | 70 | 431.0982 | - | 2 | 2
19 | BILIK PEGAWAI 2 | 27 | 70 | 290.628 | - | 2.5 | 1
20 | BILIK MESYUARAT UTAMA | 79.5 | 70 | 855.738 | 6.3054 | 2.5 | 3

## PF Correction
Capacitor | Capacitor Output (Kvar)
Stages | Switching Programme
| (a) | (b) | (C) | (d) | (e ) | (f)
1 | 5 | 5 | 5 | 5 | 5 | 5
2 | 5 | 5 | 5 | 10 | 10 | 10
3 | 5 | 10 | 10 | 10 | 20 | 20
4 | 5 | 10 | 10 | 10 | 20 | 40
5 | 5 | 10 | 20 | 10 | 20 | 40
6 | 5 | 10 | 20 | 10 | 20 | 40
7 | 5 | 10 | 20 | 10 | 20 | 40
8 | 5 | 10 | 20 | 10 | 20 | 40
9 | 5 | 10 | 20 | 10 | 20 | 40
10 | 5 | 10 | 20 | 10 | 20 | 40
11 | 5 | 10 | 20 | 10 | 20 | 40
12 | 5 | 10 | 20 | 10 | 20 | 40
13 | 5 | 10 | 20 | 10 | 20
14 | 5 | 10 | 20 | 10 | 20
Total | 70 | 130 | 230 | 135 | 255 | 395
Capacitor | Capacitor | Capacitor | CB | Selected CB Rating (A) | Contactor Current (+35%) (A) | Slected Contactor Rating (A)
Stages | Output (Kvar) | Current (A) | Current (+55%) (A)
1 | 5 | 4.19 | 6.49 | 30 | 5.66 | 16
2 | 10 | 8.38 | 12.99 | 30 | 11.31 | 16
3 | 20 | 16.76 | 25.97 | 30 | 22.62 | 25
4 | 40 | 33.52 | 51.95 | 60 | 45.25 | 63
5 | 40 | 33.52 | 51.95 | 60 | 45.25 | 63
6 | 40 | 33.52 | 51.95 | 60 | 45.25 | 63
7 | 40 | 33.52 | 51.95 | 60 | 45.25 | 63
8 | 40 | 33.52 | 51.95 | 60 | 45.25 | 63
9 | 40 | 33.52 | 51.95 | 60 | 45.25 | 63
10 | 40 | 33.52 | 51.95 | 60 | 45.25 | 63
11 | 40 | 33.52 | 51.95 | 60 | 45.25 | 63
12 | 40 | 33.52 | 51.95 | 60 | 45.25 | 63
|  | Total current (A) | CB current (30%) (A) | Selected CB Rating (A)
|  | 322.58 | 419.354 | 630