## JWPN TCL LAMPU (hidden)
BLOK PENTADBIRAN DAN AKTIVITI
PELAN SILING LANTAI BAWAH
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Lamp type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | Bilik Seminar 3 | Rhea Low Bright 2x 36 Flouresent Lamp | 4 | 84 | 336 | 0.8 | 268.8 | 1120 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 | 33.3333 |  |  | 6 | 1.5mm
1.5mm
Y1 | Bilik Seminar 4 | Rhea Low Bright 2x 36 Flouresent Lamp | 4 | 84 | 336 | 0.8 | 268.8 |  | 1120 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
B1 | Bilik Seminar 6 | Rhea Low Bright 2x 36 Flouresent Lamp | 4 | 84 | 336 | 0.8 | 268.8 |  |  | 1120 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
R2 | Bilik Seminar 2 | Rhea Low Bright 2x 36 Flouresent Lamp | 4 | 84 | 336 | 0.8 | 268.8 | 1120 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 | 33.3333 |  |  | 6 | 1.5mm
Y2 | Bilik Seminar 5 | Rhea Low Bright 2x 36 Flouresent Lamp | 4 | 84 | 336 | 0.8 | 268.8 |  | 1120 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
B2 | Bilik Seminar 1 | Rhea Low Bright 2x 36 Flouresent Lamp | 6 | 84 | 504 | 0.8 | 403.2 |  |  | 1680 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
R3 | Bilik Rehat | Rhea Low Bright 2x 36 Flouresent Lamp | 3 | 84 | 252 | 0.8 | 201.6 | 840 |  |  | 6 | 1.5mm
| Minuman Ringan | Rhea Low Bright 2x 36 Flouresent Lamp | 3 | 84 | 252 | 0.8 | 201.6 | 840 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 | 66.6667 |  |  | 6 | 1.5mm
Y3 | Coridor 1 | Project Batern 1x 36 Flouresent Lamp | 2 | 42 | 84 | 0.8 | 67.2 |  | 280 |  | 6 | 1.5mm
| Coridor 2 | Project batern 1x 36 Flouresent Lamp | 3 | 42 | 126 | 0.8 | 100.8 |  | 420 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 |  | 66.6667 |  | 6 | 1.5mm
B3 | Tandas Lelaki | Rhea Low Bright 3x 18 Flouresent Lamp | 2 | 72 | 144 | 0.8 | 115.2 |  |  | 480 | 6 | 1.5mm
| Tandas Kakitangan Lelaki | Rhea Low Bright 3x 18 Flouresent Lamp | 1 | 72 | 72 | 0.8 | 57.6 |  |  | 240 | 6 | 1.5mm
| Tandas Orang Cacat | Rhea Low Bright 3x 18 Flouresent Lamp | 1 | 72 | 72 | 0.8 | 57.6 |  |  | 240 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 3 | 10 | 30 | 0.8 | 24 |  |  | 100 | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 3 | 20 | 60 | 0.8 | 48 |  |  | 200 | 6 | 1.5mm
| Exhaust Fan | Exhaust fan | 1 | 70 | 70 | 0.8 | 56 |  |  | 233.3333 | 6 | 1.5mm
R4 | Stor | Rhea Low Bright 3x 18 Flouresent Lamp | 2 | 72 | 144 | 0.8 | 115.2 | 480 |  |  | 6 | 1.5mm
| Bilik Keyphone | Rhea Low Bright 3x 18 Flouresent Lamp | 4 | 72 | 288 | 0.8 | 230.4 | 960 |  |  | 6 | 1.5mm
| Pantry | Rhea Low Bright 3x 18 Flouresent Lamp | 1 | 72 | 72 | 0.8 | 57.6 | 240 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 3 | 10 | 30 | 0.8 | 24 | 100 |  |  | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 2 | 20 | 40 | 0.8 | 32 | 133.3333 |  |  | 6 | 1.5mm
Y4 | Pejabat PBSD | Rhea Low Bright 3x 18 Flouresent Lamp | 10 | 72 | 720 | 0.8 | 576 |  | 2400 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 |  | 66.6667 |  | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 1 | 20 | 20 | 0.8 | 16 |  | 66.6667 |  | 6 | 1.5mm
B4 | Pejabat PBSD | Rhea Low Bright 3x 18 Flouresent Lamp | 10 | 72 | 720 | 0.8 | 576 |  |  | 2400 | 6 | 1.5mm
R5 | Pejabat PBSD | Rhea Low Bright 3x 18 Flouresent Lamp | 10 | 72 | 720 | 0.8 | 576 | 2400 |  |  | 6 | 1.5mm
Y5 | Pejabat PBSD | Rhea Low Bright 3x 18 Flouresent Lamp | 10 | 72 | 720 | 0.8 | 576 |  | 2400 |  | 6 | 1.5mm
B5 | Bilik Mesyuarat | Rhea Low Bright 3x 18 Flouresent Lamp | 6 | 72 | 432 | 0.8 | 345.6 |  |  | 1440 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 1 | 20 | 20 | 0.8 | 16 |  |  | 66.6667 | 6 | 1.5mm
R6 | Bilik Mesyuarat | Rhea Low Bright 3x 18 Flouresent Lamp | 6 | 72 | 432 | 0.8 | 345.6 | 1440 |  |  | 6 | 1.5mm
Y6 | Pejabat NGO | Rhea Low Bright 3x 18 Flouresent Lamp | 9 | 72 | 648 | 0.8 | 518.4 |  | 2160 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 1 | 20 | 20 | 0.8 | 16 |  | 66.6667 |  | 6 | 1.5mm
B6 | Pejabat NGO | Rhea Low Bright 3x 18 Flouresent Lamp | 8 | 72 | 576 | 0.8 | 460.8 |  |  | 1920 | 6 | 1.5mm
R7 | Pejabat NGO | Rhea Low Bright 3x 18 Flouresent Lamp | 8 | 72 | 576 | 0.8 | 460.8 | 1920 |  |  | 6 | 1.5mm
Y7 | Bilik Kuliah 6 | Rhea Low Bright 2x 36 Flouresent Lamp | 8 | 84 | 672 | 0.8 | 537.6 |  | 2240 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
B7 | Bilik Kuliah 7 | Rhea Low Bright 2x 36 Flouresent Lamp | 8 | 84 | 672 | 0.8 | 537.6 |  |  | 2240 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
R8 | Bilik Kuliah 8 | Rhea Low Bright 2x 36 Flouresent Lamp | 8 | 84 | 672 | 0.8 | 537.6 | 2240 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 | 33.3333 |  |  | 6 | 1.5mm
Y8 | Bilik Kuliah 9 | Rhea Low Bright 2x 36 Flouresent Lamp | 8 | 84 | 672 | 0.8 | 537.6 |  | 2240 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
B8 | Coridor 3 | Project Batern 1x36 Flouresent Lamp | 3 | 42 | 126 | 0.8 | 100.8 |  |  | 420 | 6 | 1.5mm
| Coridor 4 | Project Batern 1x36 Flouresent Lamp | 3 | 42 | 126 | 0.8 | 100.8 |  |  | 420 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 |  |  | 66.6667 | 6 | 1.5mm
R9 | Stor NGO | Rhea Low Bright 3x 18 Flouresent Lamp | 6 | 72 | 432 | 0.8 | 345.6 | 1440 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 | 33.3333 |  |  | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 1 | 20 | 20 | 0.8 | 16 | 66.6667 |  |  | 6 | 1.5mm
Y9 | Tandas wanita | Rhea Low Bright 3x 18 Flouresent Lamp | 4 | 72 | 288 | 0.8 | 230.4 |  | 960 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 |  | 66.6667 |  | 6 | 1.5mm
| 'Keluar" Sign | 2X8W (F) "K" Sign | 2 | 20 | 40 | 0.8 | 32 |  | 133.3333 |  | 6 | 1.5mm
| Exhaust Fan | Exhaust fan | 1 | 70 | 70 | 0.8 | 56 |  | 233.3333 |  | 6 | 1.5mm
B9 | Ruang Legar 1 | 1 x 18 W Sheratan Compact Flouresent Downlight | 8 | 24 | 192 | 0.8 | 153.6 |  |  | 640 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 2 | 10 | 20 | 0.8 | 16 |  |  | 66.6667 | 6 | 1.5mm
R10 | Ruang Legar 1 | 1 x 18 W Sheratan Compact Flouresent Downlight | 8 | 24 | 192 | 0.8 | 153.6 | 640 |  |  | 6 | 1.5mm
Y10 | Ruang Legar 2 | 1 x 18 W Sheratan Compact Flouresent Downlight | 4 | 24 | 96 | 0.8 | 76.8 |  | 320 |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  | 33.3333 |  | 6 | 1.5mm
B10 | Ruang Legar 3 | 1 x 18 W Sheratan Compact Flouresent Downlight | 4 | 24 | 96 | 0.8 | 76.8 |  |  | 320 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
R11 | Tangga 1 | Project Batern 1x36 Flouresent Lamp | 1 | 42 | 42 | 0.8 | 33.6 | 140 |  |  | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 | 33.3333 |  |  | 6 | 1.5mm
B11 | Tangga 2 | Project Batern 1x36 Flouresent Lamp | 1 | 42 | 42 | 0.8 | 33.6 |  |  | 140 | 6 | 1.5mm
| Emergency Light | 1X8W (F) EL | 1 | 10 | 10 | 0.8 | 8 |  |  | 33.3333 | 6 | 1.5mm
Y11
|  |  | 247 | 3110 | 14264 |  | 11411.2 | 16353.3333 | 16560 | 14633.3333

## JWPN TCL SOKET (hidden)
BLOK PENTADBIRAN DAN AKTIVITI
PELAN SILING LANTAI BAWAH
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Socket type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | Bilik Rehat | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
| Bilik Seminar 3 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
Y1 | Bilik Seminar 1 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  | 416.6667 |  | 20 | 2.5mm
| Bilik Seminar 2 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  | 416.6667 |  | 20 | 2.5mm
B1 | Minuman Ringan | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R2 | Bilik Seminar 5 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
| Ruang Legar 1 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
Y2 | Bilik Kuliah 6 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  | 416.6667 |  | 20 | 2.5mm
| Bilik Kuliah 8 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  | 416.6667 |  | 20 | 2.5mm
B2 | Bilik Kuliah 7 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  |  | 416.6667 | 20 | 2.5mm
R3 | Coridor 4 | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
| Stor NGO | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
Y3 | Bilik Keyphone | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B3 | Bilik Keyphone | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 |  |  | 416.6667 | 20 | 2.5mm
R4 | Stor | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
| Pantry | 13A S/S/0 | 1 | 250 | 250 | 0.4 | 100 | 416.6667 |  |  | 20 | 2.5mm
Y4 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B4 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R5 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y5 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B5 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R6 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y6 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B6 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R7 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y7 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B7 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R8 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y8 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B8 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R9 | Pejabat PBSD | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y9 | Bilik Mesyuarat | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B9 | Bilik Mesyuarat | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R10 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y10 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B10 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R11 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y11 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B11 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
R12 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 | 833.3333 |  |  | 20 | 2.5mm
Y12 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  | 833.3333 |  | 20 | 2.5mm
B12 | Pejabat NGO | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 833.3333 | 20 | 2.5mm
TOTAL |  |  | 70 | 10500 | 17500 |  | 7000 | 10000 | 10000 | 9166.6667

## SOKET With Cucko-GROUND FLOOR
GREEN BULIDING
GROUND FLOOR - With Cuckoo Dispenser
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Socket type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 (Ring) | Bilik Server | 13A S/S/O | 5 | 250 | 1250 | 0.4 | 500 | 2557.5448 |  |  | 32 | 2.5mm
| Timbalan Dekan | 13A S/S/O | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358
Y1 (Ring) | Bilik Dekan | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 |  | 2557.5448 |  | 32 | 2.5mm
| BILIK MESYUARAT | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 |  | 2557.5448
B1 (Ring) | BILIK CETAK | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 |  |  | 2557.5448 | 32 | 2.5mm
| BILIK SETOR 1 | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  |  | 1534.5269
R2 (Ring) | PENOLONG DAFTAR 1 | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 | 1534.5269 |  |  | 32 | 2.5mm
| BILIK PANTRI 1 | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 | 2557.5448
Y2 (Ring) | BILIK TETAMU | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  | 1534.5269 |  | 32 | 2.5mm
| PENOLONG DAFTAR 2 | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  | 1534.5269
B2 (Ring) | PUSAT KEJURUTERAAN 1 | 13 A S/S/O | 10 | 250 | 2500 | 0.4 | 1000 |  |  | 5115.0895 | 32 | 2.5mm
R3 (Ring) | UTILITI | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 | 1534.5269 |  |  | 32 | 2.5mm
| BILIK SWITCHBOARD (ER) | 13 A S/S/O | 1 | 250 | 250 | 0.4 | 100 | 511.509
| BILIK SETOR 2 | 13 A S/S/O | 1 | 250 | 250 | 0.4 | 100 | 511.509
| TANDAS LELAKI | 13 A S/S/O | 1 | 250 | 250 | 0.4 | 100 | 511.509
| SURAU (P) | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 | 1023.0179
| TANDAS PEREMPUAN | 13 A S/S/O | 1 | 250 | 250 | 0.4 | 100 | 511.509
Y3 (Ring) | PUSAT KEJURUTERAAN 1 | 13 A S/S/O | 10 | 250 | 2500 | 0.4 | 1000 |  | 5115.0895 |  | 32 | 2.5mm
B3 (Radial) | Cuckoo Dispenser |  | 1 | 2400 | 2400 | 0.4 | 960 |  |  | 4910.4859 | 32 | 2.5mm
| R. TANGGA/LEGAR | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 |  |  | 1023.0179
R4 (Ring) | SURAU (L) | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 | 1023.0179 |  |  | 32 | 2.5mm
| PUSAT KEJURUTERAAN 2 | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 | 1023.0179
| BILIK PANTRI 2 | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 | 2557.5448
B4 (Ring) | Car Porch | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 |  |  | 1023.0179 | 32 | 2.5mm
| Corridors | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  |  | 1534.5269
Y4 (Ring) | BILIK MESYUARAT 2 | 13 A S/S/O | 10 | 250 | 2500 | 0.4 | 1000 |  | 5115.0895 |  | 32 | 2.5mm
TOTAL |  |  | 97 | 8650 | 26400 |  | 10560 | 17902.8133 | 18414.3223 | 17698.2097

## TCL SOKET KOSONG-GROUND FLOOR
GREEN BULIDING
GROUND FLOOR
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Socket type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 (Ring) | Bilik Server | 13A S/S/O | 5 | 250 | 1250 | 0.4 | 500 | 2557.5448 |  |  | 32 | 2.5mm
| Timbalan Dekan | 13A S/S/O | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358
Y1 (Ring) | Bilik Dekan | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 |  | 2557.5448 |  | 32 | 2.5mm
| BILIK MESYUARAT | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 |  | 2557.5448
B1 (Ring) | BILIK CETAK | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 |  |  | 2557.5448 | 32 | 2.5mm
| BILIK SETOR 1 | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  |  | 1534.5269
R2 (Ring) | PENOLONG DAFTAR 1 | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 | 1534.5269 |  |  | 32 | 2.5mm
| BILIK PANTRI 1 | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 | 2557.5448
Y2 (Ring) | PUSAT KEJURUTERAAN 2 | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 |  | 1023.0179 |  | 32 | 2.5mm
| BILIK TETAMU | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  | 1534.5269
| PENOLONG DAFTAR 2 | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  | 1534.5269
| R. TANGGA/LEGAR | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 |  | 1023.0179
B2 (Ring) | PUSAT KEJURUTERAAN 1 | 13 A S/S/O | 10 | 250 | 2500 | 0.4 | 1000 |  |  | 5115.0895 | 32 | 2.5mm
R3 (Ring) | UTILITI | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 | 1534.5269 |  |  | 32 | 2.5mm
| BILIK SWITCHBOARD (ER) | 13 A S/S/O | 1 | 250 | 250 | 0.4 | 100 | 511.509
| BILIK SETOR 2 | 13 A S/S/O | 1 | 250 | 250 | 0.4 | 100 | 511.509
| TANDAS LELAKI | 13 A S/S/O | 1 | 250 | 250 | 0.4 | 100 | 511.509
| TANDAS PEREMPUAN | 13 A S/S/O | 1 | 250 | 250 | 0.4 | 100 | 511.509
Y3 (Ring) | PUSAT KEJURUTERAAN 1 | 13 A S/S/O | 10 | 250 | 2500 | 0.4 | 1000 |  | 5115.0895 |  | 32 | 2.5mm
B3 (Ring) | BILIK MESYUARAT 2 | 13 A S/S/O | 10 | 250 | 2500 | 0.4 | 1000 |  |  | 5115.0895 | 32 | 2.5mm
R4 (Ring) | SURAU (P) | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 | 1023.0179 |  |  | 32 | 2.5mm
| SURAU (L) | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 | 1023.0179
| BILIK PANTRI 2 | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 | 2557.5448
B4 (Ring) | Car Porch | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 |  |  | 1023.0179 | 32 | 2.5mm
| Corridors | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  |  | 1534.5269
TOTAL |  |  | 96 | 6250 | 24000 |  | 9600 | 16879.7954 | 15345.2685 | 16879.7954

## AC-GROUND FLOOR
GREEN BULIDING
GROUND FLOOR
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | AIR CON Type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | BILIK SERVER | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 | 5575.4476 |  |  | 32 | 4mm
Y1 | TIMBALAN DEKAN | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4mm
B1 | BILIK DEKAN | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 |  |  | 8849.1049 | 32 | 4mm
R2 | BILIK CETAK | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 | 8849.1049 |  |  | 32 | 4mm
Y2 | PENOLONG DAFTAR 1 | Hisense AN10DBG2 (1HP) | 1 | 890 | 890 | 1 | 890 |  | 4552.4297 |  | 32 | 4mm
B2 | PENOLONG DAFTAR 2 | Hisense AN10DBG2 (1HP) | 1 | 890 | 890 | 1 | 890 |  |  | 4552.4297 | 32 | 4mm
R3 | BILIK TETAMU | Hisense AN10DBG2 (1HP) | 1 | 890 | 890 | 1 | 890 | 4552.4297 |  |  | 32 | 4mm
Y3 | BILIK MESYUARAT 1 | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 |  | 8849.1049 |  | 32 | 4mm
B3 | BILIK MESYUARAT BESAR 2 | Hisense AN25DBG (2.5HP) | 1 | 2186 | 2186 | 1 | 2186 |  |  | 11181.5857 | 32 | 4mm
R4 | BILIK MESYUARAT BESAR 2 | Hisense AN25DBG (2.5HP) | 1 | 2186 | 2186 | 1 | 2186 | 11181.5857 |  |  | 32 | 4mm
Y4 | BILIK MESYUARAT BESAR 2 | Hisense AN25DBG (2.5HP) | 1 | 2186 | 2186 | 1 | 2186 |  | 11181.5857 |  | 32 | 4mm
B4 | PUSAT KEJURUTERAAN 1 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  |  | 5575.4476 | 32 | 4mm
R5 | PUSAT KEJURUTERAAN 1 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 | 5575.4476 |  |  | 32 | 4mm
Y5 | PUSAT KEJURUTERAAN 1 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4mm
B5 | PUSAT KEJURUTERAAN 1 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  |  | 5575.4476 | 32 | 4mm
R6 | SURAU (L) | Hisense AN10DBG2 (1 HP) | 1 | 850 | 850 | 1 | 850 | 4347.8261 |  |  | 32 | 4mm
Y6 | UTILITI | Hisense AN20DBG (2 HP) | 1 | 1730 | 1730 | 1 | 1730 |  | 8849.1049 |  | 32 | 4mm
B6 | PUSAT KEJURUTERAAN 2 | Hisense AN10DBG2 (1HP) | 1 | 850 | 850 | 1 | 850 |  |  | 4347.8261 | 32 | 4mm
R7 | SURAU (P) | Hisense AN10DBG2 (1 HP) | 1 | 850 | 850 | 1 | 850 | 4347.8261 |  |  | 32 | 4mm
B7 | PUSAT KEJURUTERAAN 2 | Hisense AN10DBG2 (1HP) | 1 | 850 | 850 | 1 | 850 |  |  | 4347.8261 | 32 | 4mm
|  |  | 20 | 26088 | 26088 |  | 26088 | 44429.6675 | 44583.1202 | 44429.6675
LOAD BALANCING (15% JKR STD)
[5 empty] | 44480.82 |  |  | -0.12 | 0.23 | 0.12

## GROUND FLOOR-TCL LAMPU KOSON
GREEN BULIDING
GROUND FLOOR
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Lamp type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | BILIK SERVER | FLUORESCENT 2X36W + BALLAST 6W | 4 | 84 | 336 | 0.8 | 268.8 | 1374.9361 |  |  | 6 | 1.5mm
| TIMBALAN DEKAN | FLUORESCENT 2X36W + BALLAST 6W | 4 | 84 | 336 | 0.8 | 268.8 | 1374.9361
| CORRIDOR A | FLUORESCENT 1x36W + BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 | 343.734
Y1 | BILIK DEKAN | FLUORESCENT 2x36W + BALLAST 6W | 6 | 84 | 504 | 0.8 | 403.2 |  | 2062.4041 |  | 6 | 1.5mm
| CORRIDOR B | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 |  | 171.867
| CORRIDOR C | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 |  | 171.867
| CORRIDOR D | FLUORESCENT 1x36W + BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 |  | 343.734
B1 | BILIK CETAK | FLUORESCENT 2x36W + BALLAST 6W | 6 | 84 | 504 | 0.8 | 403.2 |  |  | 2062.4041 | 6 | 1.5mm
| BILIK STOR 1 | FLUORESCENT 1x36W + BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 |  |  | 343.734
| BILIK STOR 2 | FLUORESCENT 1x36W + BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 |  |  | 343.734
R2 | PENOLONG DAFTAR 1 | FLUORESCENT 2x36W + BALLAST 6W | 4 | 84 | 336 | 0.8 | 268.8 | 1374.9361 |  |  | 6 | 1.5mm
| CORRIDOR S | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 | 171.867
| PENOLONG DAFTAR 2 | FLUORESCENT 2x36W + BALLAST 6W | 4 | 84 | 336 | 0.8 | 268.8 | 1374.9361
| CORRIDOR E | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 | 171.867
Y2 | BILIK TETAMU | FLUORESCENT 2x36W + BALLAST 6W | 4 | 84 | 336 | 0.8 | 268.8 |  | 1374.9361 |  | 6 | 1.5mm
| UTILITI | FLUORESCENT 1x36W + BALLAST 6W | 4 | 42 | 168 | 0.8 | 134.4 |  | 687.468
| CORRIDOR G | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 |  | 171.867
| CORRIDOR H | FLUORESCENT 1x36W + BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 |  | 343.734
B2 | BILIK MESYUARAT 1 | FLUORESCENT 2x36W + BALLAST 6W | 6 | 84 | 504 | 0.8 | 403.2 |  |  | 2062.4041 | 6 | 1.5mm
| SURAU (P) | FLUORESCENT 2x36W + BALLAST 6W | 2 | 84 | 168 | 0.8 | 134.4 |  |  | 687.468
| SURAU (L) | FLUORESCENT 2x36W + BALLAST 6W | 2 | 84 | 168 | 0.8 | 134.4 |  |  | 687.468
R3 | BILIK MESYUARAT BESAR | FLUORESCENT 2x36W + BALLAST 6W | 10 | 84 | 840 | 0.8 | 672 | 3437.3402 |  |  | 6 | 1.5mm
Y3 | PUSAT KEJURUTERAAN 1 | FLUORESCENT 2x36W + BALLAST 6W | 10 | 84 | 840 | 0.8 | 672 |  | 3437.3402 |  | 6 | 1.5mm
B3 | PUSAT KEJURUTERAAN 2 | FLUORESCENT 2x36W + BALLAST 6W | 6 | 84 | 504 | 0.8 | 403.2 |  |  | 2062.4041 | 6 | 1.5mm
| CORRIDOR J | FLUORESCENT 1x36W + BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 |  |  | 343.734
| CORRIDOR K | FLUORESCENT 1x36W + BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 |  |  | 343.734
R4 | BILIK PANTRI 1 | FLUORESCENT 1x36W + BALLAST 6W | 6 | 42 | 252 | 0.8 | 201.6 | 1031.202 |  |  | 6 | 1.5mm
| BILIK PANTRI 2 | FLUORESCENT 1x36W + BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 | 343.734
| CORRIDOR L | FLUORESCENT 1x36W + BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 | 343.734
Y4 | TANDAS LELAKI | FLUORESCENT 1x18W + BALLAST 6W | 6 | 24 | 144 | 0.8 | 115.2 |  | 589.2583 |  | 6 | 1.5mm
| CORRIDOR R | FLUORESCENT 1x36W + BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 |  | 343.734
| CORRIDOR S | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 |  | 171.867
| CORRIDOR T | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 |  | 171.867
B4 | TANDAS PEREMPUAN | FLUORESCENT 1x18W + BALLAST 6W | 6 | 24 | 144 | 0.8 | 115.2 |  |  | 589.2583 | 6 | 1.5mm
| CORRIDOR O | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 |  |  | 171.867
| CORRIDOR P | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 |  |  | 171.867
| BILIK MESYUARAT BESAR | FLUORESCENT 2x36W + BALLAST 6W | 2 | 84 | 168 | 0.8 | 134.4 |  |  | 687.468
R5 | ANJUNG KERETA | FLUORESCENT 1x36W + BALLAST 6W | 5 | 42 | 210 | 0.8 | 168 | 859.335 |  |  | 6 | 1.5mm
| CORRIDOR Q | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 84 | 0.8 | 67.2 | 343.734
| CORRIDOR M | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 | 171.867
| CORRIDOR N | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 | 171.867
Y5 | R. TANGGA / LEGAR | FLUORESCENT 1x36W + BALLAST 6W | 6 | 42 | 252 | 0.8 | 201.6 |  | 1031.202 |  | 6 | 1.5mm
| BILIK PANTRI 1 | VENTILATING FAN ¦ 15TGQZ 1x25.7W | 1 | 25.7 | 25.7 | 0.8 | 20.56 |  | 105.1662
| CORRIDOR F | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 |  | 171.867
| EXIT SIGN CEILING | VKS 555/STS/RM ¦ 1x2.5W | 2 | 2.5 | 5 | 0.8 | 4 |  | 20.4604
B5 | TANDAS LELAKI | VENTILATING FAN ¦ 15TGQZ 1x25.7W | 4 | 25.7 | 102.8 | 0.8 | 82.24 |  |  | 420.665 | 6 | 1.5mm
| BILIK STOR 1 | REGULATOR CEILING FAN ¦ K12V0 1x54W | 1 | 54 | 54 | 0.8 | 43.2 |  |  | 220.9719
| BILIK STOR 2 | REGULATOR CEILING FAN ¦ K12V0 1x54W | 1 | 54 | 54 | 0.8 | 43.2 |  |  | 220.9719
| EXIT SIGN CEILING | VKS 555/STS/RM ¦ 1x2.5W | 4 | 2.5 | 10 | 0.8 | 8 |  |  | 40.9207
R6 | EMERGENCY LIGHT | VEL 330/ST ¦ 1x1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 | 49.1049 |  |  | 6 | 1.5mm
Y6 | EMERGENCY LIGHT | VEL 330/ST ¦ 1x1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 |  | 49.1049 |  | 6 | 1.5mm
B6 | EMERGENCY LIGHT | VEL 330/ST ¦ 1x1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 |  |  | 49.1049 | 6 | 1.5mm
R7 | EMERGENCY LIGHT | VEL 330/ST ¦ 1x1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 | 49.1049 |  |  | 6 | 1.5mm
Y7 | EMERGENCY LIGHT | VEL 330/ST ¦ 1x1.2W | 5 | 1.2 | 6 | 0.8 | 4.8 |  | 24.5524 |  | 6 | 1.5mm
| EXIT SIGN CEILING | VKS 555/STS/RM ¦ 1x2.5W | 5 | 2.5 | 12.5 | 0.8 | 10 |  | 51.1509
B7 | EXIT SIGN CEILING | VKS 570/WP/RM ¦ 1x2.5W | 5 | 2.5 | 12.5 | 0.8 | 10 |  |  | 51.1509 | 6 | 1.5mm
| BILIK PANTRI 2 | VENTILATING FAN ¦ 15TGQZ 1x25.7W | 1 | 25.7 | 25.7 | 0.8 | 20.56 |  |  | 105.1662
| TANDAS PEREMPUAN | VENTILATING FAN ¦ 15TGQZ 1x25.7W | 4 | 25.7 | 102.8 | 0.8 | 82.24 |  |  | 420.665
R8 | EMERGENCY LIGHT | VEL 330/ST ¦ 1x1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 | 49.1049 |  |  | 6 | 1.5mm
Y8 | PUSAT KEJURUTERAAN 1 | FLUORESCENT 2x36W + BALLAST 6W | 2 | 84 | 168 | 0.8 | 134.4 |  | 687.468 |  | 6 | 1.5mm
| CORRIDOR K | FLUORESCENT 1x36W + BALLAST 6W | 2 | 42 | 84 | 0.8 | 67.2 |  | 343.734
| Switchboard Room (ER) | FLUORESCENT 1x36W + BALLAST 6W | 1 | 42 | 42 | 0.8 | 33.6 |  | 171.867
| EXIT SIGN CEILING | VKS 570/WP/RM ¦ 1x2.5W | 5 | 2.5 | 12.5 | 0.8 | 10 |  | 51.1509
|  |  | 229 | 2756.5 | 9255.5 |  | 7404.4 | 13037.3402 | 12749.6675 | 12087.1611

## AC CALCULATION - GROUND FLOOR
No | Room (EN) | Room (BM) | Area (m²) | Heat Factor | Area (ft²) | Calculated HP | Final AC Selection | Qty AC | Remarks
1 | Server Room | BILIK SERVER | 19.92 | 60 | 214.4189 | 1.3542 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5 HP)
2 | Deputy Dean Office | TIMBALAN DEKAN | 19.92 | 60 | 214.4189 | 1.3542 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5 HP)
3 | Dean Office | BILIK DEKAN | 24 | 60 | 258.336 | 1.6316 | 2 HP | 1 | Hisense AN20DBG (2 HP)
4 | Printing Room | BILIK CETAK | 27.72 | 60 | 298.3781 | 1.8845 | 2 HP | 1 | Hisense AN20DBG (2 HP)
5 | Store Room | BILIK STOR | 20.2 | 60 | 217.4328 | - | - | 1 | Ceiling Fan K12V0
6 | Assistant Registrar Office | PENOLONG DAFTAR | 12.935 | 60 | 139.2323 | 0.87936 | 1 HP | 1 | Hisense AN10DBG2 (1 HP)
7 | Pantry Room 1 | BILIK PANTRI 1 | 13.0146 |  | 140.0892 | - | - | 1 | Exhaust Fan 15TGQZ
8 | Assistant Registrar Office 2 | PENOLONG DAFTAR 2 | 12.935 | 60 | 139.2323 | 0.87936 | 1 HP | 1 | Hisense AN10DBG2 (1 HP)
9 | Guest Room | BILIK TETAMU | 13.0146 | 60 | 140.0892 | 0.88477 | 1 HP | 1 | Hisense AN10DBG2 (1 HP)
10 | Meeting Room | BILIK MESYUARAT | 24 | 70 | 258.336 | 1.9035 | 2 HP | 1 | Hisense AN20DBG (2 HP)
11 | Switchboard Room (ER) | BILIK SWITCHBOARD (ER) | 5.3 | 60 | 57.0492 | - | - | 1 | Ceiling Fan K12V0
12 | Store Room 2 | BILIK STOR | 6.09 | 60 | 65.5528 | - | - | 1 | Ceiling Fan K12V0
13 | Meeting Room Large | BILIK MESYUARAT | 79.975 | 70 | 860.8509 | 6.3431 | 2.5 HP | 3 | Hisense AN25DBG2 (2.5 HP)
14 | Staircase / Lobby | R. TANGGA / LEGAR | 48.6 | 60 | 523.1304 | 3.304 | 1 HP | 4 | Hisense AN10DBG (1 HP)
15 | Utility Room | UTILITI | 22.275 | 60 | 239.7681 | 1.5143 | 2 HP | 1 | Hisense AN20DBG (2 HP)
16 | Engineering Center 1 | PUSAT KEJURUTERAAN 1 | 75 | 70 | 807.3 | 5.9485 | 1.5 HP | 4 | Hisense AN13DBG2 (1.5 HP)
17 | Engineering Center 2 | PUSAT KEJURUTERAAN 2 | 25.15 | 70 | 270.7146 | 1.9947 | 1 HP | 2 | Hisense AN10DBG2 (1 HP)
18 | Male Toilet | TANDAS LELAKI | 18.675 |  | 201.0177 | - | - | 4 | Exhaust Fan 15TGQZ
19 | Female Toilet | TANDAS PEREMPUAN | 18.3015 |  | 196.9973 | - | - | 4 | Exhaust Fan 15TGQZ
20 | Female Prayer Room | SURAU (P) | 9.69 | 70 | 104.3032 | 0.76855 | 1 HP | 1 | Hisense AN10DBG2 (1 HP)
21 | Male Prayer Room | SURAU (L) | 8.715 | 70 | 93.8083 | 0.69122 | 1 HP | 1 | Hisense AN10DBG2 (1 HP)
22 | Pantry Room 2 | BILIK PANTRI 2 | 15.9 | 60 | 171.1476 | 1.0809 | 1 HP | 1 | Hisense AN10DBG2 (1 HP)
23 | Car Porch Area | ANJUNG KERETA | 69.8906 |  | 752.303 | - | - | - | -

## 1ST FLOOR - TCL SOKET KOSON
GREEN BULIDING
FIRST FLOOR
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Socket type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | Bilik Server | 13A S/S/O | 5 | 250 | 1250 | 0.4 | 500 | 2557.5448 |  |  | 32 | 2.5mm
| BILIK CETAK | 13A S/S/O | 2 | 250 | 500 | 0.4 | 200 | 1023.0179
| BILIK SETOR 1 | 13A S/S/O | 3 | 250 | 750 | 0.4 | 300 | 1534.5269
Y1 | BILIK MESYUARAT | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 |  | 2557.5448 |  | 32 | 2.5mm
| Timbalan Dekan | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 |  | 2557.5448
B1 | Bilik Dekan | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 |  |  | 2557.5448 | 32 | 2.5mm
| BILIK TETAMU | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 |  |  | 1023.0179
| PENOLONG DAFTAR 1 | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  |  | 1534.5269
R2 | PUSAT KEJURUTERAAN 1 | 13 A S/S/O | 10 | 250 | 2500 | 0.4 | 1000 | 5115.0895 |  |  | 32 | 2.5mm
Y2 | RUANG STAF | 13 A S/S/O | 8 | 250 | 2000 | 0.4 | 800 |  | 4092.0716 |  | 32 | 2.5mm
B2 | UTILITI | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  |  | 1534.5269 | 32 | 2.5mm
| PUSAT 1 | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  |  | 1534.5269
| TANDAS LELAKI | 13 A S/S/O | 1 | 250 | 250 | 0.4 | 100 |  |  | 511.509
| TANDAS PEREMPUAN | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 |  |  | 1023.0179
R3 | PENYELARAS PUSAT 1 | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 | 1534.5269 |  |  | 32 | 2.5mm
| PENYELARAS PUSAT 2 | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 | 1534.5269
Y3 | R. TANGGA/LEGAR | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  | 1534.5269 |  | 32 | 2.5mm
| PUSAT 2 | 13 A S/S/O | 4 | 250 | 1000 | 0.4 | 400 |  | 2046.0358
| BILIK SETOR 2 | 13 A S/S/O | 3 | 250 | 750 | 0.4 | 300 |  | 1534.5269
B3 | KORIDOR-1 | 13 A S/S/O | 2 | 250 | 500 | 0.4 | 200 |  |  | 1023.0179 | 32 | 2.5mm
| KORIDOR-2 | 13 A S/S/O | 5 | 250 | 1250 | 0.4 | 500 |  |  | 2557.5448
R4 | PUSAT KEJURUTERAAN 2 | 13 A S/S/O | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  | 32 | 2.5mm
TOTAL |  |  | 84 | 5500 | 21000 |  | 8400 | 13299.2327 | 14322.2506 | 13299.2327

## 1ST FLOOR -AC
GREEN BULIDING
FIRST FLOOR
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | AC Power Unit [HP] |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | Bilik Server | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 | 8849.1049 |  |  | 32 | 4 mm
Y1 | Timbalan Dekan | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 |  | 8849.1049 |  | 32 | 4 mm
B1 | Mesyuarat Dekan | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 |  |  | 8849.1049 | 32 | 4 mm
R2 | Dekan | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 | 8849.1049 |  |  | 32 | 4 mm
Y2 | PUSAT-2 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4 mm
B2 | Cetak | Hisense AN10DBG2 (1HP) | 1 | 850 | 850 | 1 | 850 |  |  | 4347.8261 | 32 | 4 mm
R3 | Pusat Kejuruuteraan (6) | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 | 8849.1049 |  |  | 32 | 4 mm
Y3 | Pusat-1 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4 mm
B3 | Pusat Kejuruuteraan (4) | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 |  |  | 8849.1049 | 32 | 4 mm
R4 | TEAMU | Hisense AN10DBG2 (1HP) | 1 | 850 | 850 | 1 | 850 | 4347.8261 |  |  | 32 | 4 mm
Y4 | PENYELARAS PUSAT-1 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4 mm
B4 | Pusat Kejuruuteraan (1) | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 |  |  | 8849.1049 | 32 | 4 mm
R5 | Pusat Kejuruuteraan (3) | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 | 8849.1049 |  |  | 32 | 4 mm
Y5 | Pusat Kejuruuteraan (2) | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 |  | 8849.1049 |  | 32 | 4 mm
B5 | PENYELARAS PUSAT-2 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  |  | 5575.4476 | 32 | 4 mm
R6 | UTILITI | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 | 5575.4476 |  |  | 32 | 4 mm
Y6 | Pusat Kejuruuteraan (5) | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 |  | 8849.1049 |  | 32 | 4 mm
B6 | PENOLONG | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  |  | 5575.4476 | 32 | 4 mm
TOTAL |  |  | 18 | 25540 | 25540 | 18 | 25540 | 45319.6931 | 43273.6573 | 42046.0358

## 1ST FLOOR - TCL LAMPU KOSON
GREEN BULIDING
FIRST FLOOR
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Lamp type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | Timblan Pengarah | Fluorescent 2 x 36W+Ballast 6 W | 4 | 84 | 336 | 0.8 | 268.8 | 1374.9361 |  |  | 6 | 1.5 mm
| Bilik Server | Fluorescent 1 x 36W+Ballast 6 W | 3 | 42 | 126 | 0.8 | 100.8 | 515.601 |  |  |  | 1.5 mm
| Bilik Setor | Fluorescent 1 x 36W+Ballast 6 W | 3 | 42 | 126 | 0.8 | 100.8 | 515.601 |  |  |  | 1.5 mm
Y1 | Bilik Pantri | Fluorescent 1 x 36W+Ballast 6 W | 2 | 42 | 84 | 0.8 | 67.2 |  | 343.734 |  | 6 | 1.5 mm
| Bilik Bincang | Fluorescent 2 x 36W +Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  |  | 1.5 mm
B1 | Bilik Pengarah | Fluorescent 2 x 36W +Ballast 6 W | 5 | 84 | 420 | 0.8 | 336 |  |  | 1718.6701 | 6 | 1.5 mm
| Bilik Tetamu | Fluorescent 2 x 36W +Ballast 6 W | 5 | 84 | 420 | 0.8 | 336 |  |  | 1718.6701 |  | 1.5 mm
R2 | Penolong Pendafar | Fluorescent 2 x 36W +Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 | 1031.202 |  |  | 6 | 1.5 mm
| Penolong Pendafar | Fluorescent 2 x 36W +Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 | 1031.202 |  |  |  | 1.5 mm
Y2 | Bilik Mesyurat | Fluorescent 2 x 36W +Ballast 6 W | 6 | 84 | 504 | 0.8 | 403.2 |  | 2062.4041 |  | 6 | 1.5 mm
B2 | Tandas | Fluorescent 1 x 36W +Ballast 6 W | 8 | 42 | 336 | 0.8 | 268.8 |  |  | 1374.9361 | 6 | 1.5 mm
R3 | R. Tangga/ Legar | Fluorescent 1 x 36W +Ballast 6 W | 2 | 42 | 84 | 0.8 | 67.2 | 343.734 |  |  | 6 | 1.5 mm
| Bikil Setor | Fluorescent 1 x 36W +Ballast 6 W | 3 | 42 | 126 | 0.8 | 100.8 | 515.601 |  |  |  | 1.5 mm
Y3 | Bilik Rundingan-1 | Fluorescent 2 x 36W+Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  | 6 | 1.5 mm
| Bilik Rundingan-2 | Fluorescent 2 x 36W +Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  |  | 1.5 mm
| Bilik Rundingan-3 | Fluorescent 2 x 36W +Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  |  | 1.5 mm
B3 | Pusat Kejuruuteraan -1 | Fluorescent 2 x 36W +Ballast 6 W | 8 | 84 | 672 | 0.8 | 537.6 |  |  | 2749.8721 | 6 | 1.5 mm
R4 | Koridor | Fluorescent 1 x 36W +Ballast 6 W | 9 | 42 | 378 | 0.8 | 302.4 | 1546.8031 |  |  | 6 | 1.5 mm
Y4 | Pusat Kejuruuteraan -1 | Fluorescent 2 x 36W +Ballast 6 W | 8 | 84 | 672 | 0.8 | 537.6 |  | 2749.8721 |  | 6 | 1.5 mm
B4 | Bilik Rundingan-4 | Fluorescent 2 x 36W +Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 |  |  | 1031.202 | 6 | 1.5 mm
R5 | TANDAS FAN | Ceiling Mounted Ventilating Fans | 6 | 25.7 | 154.2 | 0.8 | 123.36 | 630.9974 |  |  | 6 | 1.5 mm
| EMERGENCY | VEL 330/ST 1X1.2W | 3 | 1.2 | 3.6 | 0.8 | 2.88 | 14.7315 |  |  |  | 1.5 mm
Y5 | EMERGENCY | VEL 330/ST 1X1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 |  | 49.1049 |  | 6 | 1.5 mm
B5 | EMERGENCY | VEL 330/ST 1X1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 |  |  | 49.1049 | 6 | 1.5 mm
R6 | EXIT SIGN CEILING | VSK 570/WP/RM 1X2.5W | 8 | 2.5 | 20 | 0.8 | 16 | 81.8414 |  |  | 6 | 1.5 mm
Y6 | EXIT SIGN CEILING | VSK 570/WP/RM 1X2.5W | 10 | 2.5 | 25 | 0.8 | 20 |  | 102.3018 |  | 6 | 1.5 mm
B6 | CELLING FAN | REGULATOR FANS 1X54W | 2 | 25.7 | 51.4 | 0.8 | 41.12 |  |  | 210.3325 | 6 | 1.5 mm
TOTAL |  |  | 136 | 1446 | 6326.2 |  | 5060.96 | 7602.2506 | 9432.2251 | 8852.7877

## 1ST FLOOR - AC CALCULATION
GREEN BULIDING
FIRST FLOOR
No | Room (EN) | Room (BM) | Area (m²) | Heat Factor | Area (ft²) | Calculated HP | Final AC Selection | Qty AC | Remarks
1 | Server Room | Bilik Server | 20.6 | 70 | 221.7384 | 1.6339 | 2.0 HP | 1 | Hisense AN20DBG (2HP)
2 | Assitant Dean | Timbalan Dekan | 19.0221 | 70 | 204.7539 | 1.5087 | 2.0 HP | 1 | Hisense AN20DBG (2HP)
3 | Dean Meeting | Mesyuarat Dekan | 23.0677 | 70 | 248.3007 | 1.8296 | 2.0 HP | 1 | Hisense AN20DBG (2HP)
4 | Dean Meeting | Dekan | 23.92 | 70 | 257.4749 | 1.8972 | 2.0 HP | 1 | Hisense AN20DBG (2HP)
5 | Guest Room | Tetamu | 14.691 | 60 | 158.1339 | 0.99874 | 1.0 HP | 1 | Hisense AN10DBG2 (1HP)
6 | Ass Registar | Penolong Daftar | 13.1 | 70 | 141.0084 | 1.039 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
7 | Cetak | Cetak | 9.1 | 70 | 97.9524 | 0.72175 | 1.0HP | 1 | Hisense AN10DBG2 (1HP)
8 | Store Room | Setor | 12.44 | 60 | 133.9042 | 0.84571 | Celling fan | - | No AC required
9 | Pusat 1 | Pusat 1 | 15.852 | 70 | 170.6309 | 1.2573 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
10 | Engineering Area | Pusat Kejuruteraan | 176 | 60 | 1894.464 | 11.965 | 2.0 HP | 6 | Hisense AN20DBG (2HP)
11 | Toilet (M) | Tandas (L) | 18.3375 | 60 | 197.3848 | 1.2466 | Exhaust Fan | - | No AC required
12 | Toilet (F) | Tandas (P) | 18.3375 | 60 | 197.3848 | 1.2466 | Exhaust Fan | - | No AC required
13 | Stairs | Tangga | 22.275 | 60 | 239.7681 | 1.5143 | 1.5HP | 1 | Hisense AN13DBG1 (1.5HP)
14 | Store Room | Bilik Setor | 11.5 | 70 | 123.786 | 0.91211 | Celling fan | - | No AC required
15 | Coordination Centre | Pusat Penyelaras 1 | 15.048 | 60 | 161.9767 | 1.023 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
16 | Utility | Utiliti | 17.57 | 60 | 189.1235 | 1.1945 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
17 | Coordination Centre | Pusat Penyelaras 2 | 16.4902 | 70 | 177.5011 | 1.3079 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
18 | Pusat 2 | Center | 16.4902 | 70 | 177.5011 | 1.3079 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
19 | Concrete Roof | Bumbung Konkrit | 50.196 | 70 | 540.3097 | 3.9812 | 1.0 HP | 1 | Hisense AN10DBG2 (1HP)

## 2ND FLOOR-TCL SOKET KOSON
GREEN BULIDING
2ND FLOOR
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Socket type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | Timbalan Pengarah | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  | 32 | 2.5mm
| Bilik Server | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  | 32 | 2.5mm
Y1 | Bilik Pengarah | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 |  | 2046.0358 |  | 32 | 2.5mm
| Bilik Tetamu | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 |  | 2046.0358 |  | 32 | 2.5mm
B1 | Bilik Setor | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 |  |  | 2046.0358 | 32 | 2.5mm
| Bilik Pantir | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 |  |  | 2046.0358 | 32 | 2.5mm
R2 | Penolong Pendaftar 1 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  | 32 | 2.5mm
| Penolong Pendaftar 2 | 13A S/S/1 | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  | 32 | 2.5mm
Y2 | Bilik Mesyuarat -1 | 13A S/S/0 | 10 | 250 | 2500 | 0.4 | 1000 |  | 5115.0895 |  | 32 | 2.5mm
B2 | Koridor -2 | 13A S/S/2 | 3 | 250 | 750 | 0.4 | 300 |  |  | 1534.5269 | 32 | 2.5mm
| Tandas | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 1023.0179 | 32 | 2.5mm
R3 | Bilik Rundingan 1 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  | 32 | 2.5mm
| Bilik Rundingan 1 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 | 2046.0358 |  |  | 32 | 2.5mm
Y3 | Bilik Rundingan 3 | 13A S/S/2 | 4 | 250 | 1000 | 0.4 | 400 |  | 2046.0358 |  | 32 | 2.5mm
| Bilik Rundingan 4 | 13A S/S/3 | 4 | 250 | 1000 | 0.4 | 400 |  | 2046.0358 |  | 32 | 2.5mm
B3 | Bilik Setor | 13A S/S/0 | 2 | 250 | 500 | 0.4 | 200 |  |  | 1023.0179 | 32 | 2.5mm
| Koridor -1 | 13A S/S/0 | 4 | 250 | 1000 | 0.4 | 400 |  |  | 2046.0358 | 32 | 2.5mm
R4 | Bilik Mesyuarat -2 | 13A S/S/0 | 3 | 250 | 750 | 0.4 | 300 | 1534.5269 |  |  | 32 | 2.5mm
Y4 | Bilik Baincang | 13A S/S/3 | 4 | 250 | 1000 | 0.4 | 400 |  | 2046.0358 |  | 32 | 2.5mm
B4 | Pusat Kejuruteraan | 13A S/S/5 | 8 | 250 | 2000 | 0.4 | 800 |  |  | 4092.0716 | 32 | 2.5mm
TOTAL |  |  | 84 | 5000 | 21000 |  | 8400 | 13810.7417 | 15345.2685 | 13810.7417

## 2ND FLOOR-AC
GREEN BULIDING
2ND FLOOR
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | AC Power Unit [HP] |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | Timblan Pengarah | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 | 5575.4476 |  |  | 32 | 4mm
Y1 | Bilik Server | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4 mm
B1 | Bilik Pengarah | Hisense AN20DBG (2HP) | 1 | 1730 | 1730 | 1 | 1730 |  |  | 8849.1049 | 32 | 4 mm
R2 | Bilik Bincang | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 | 5575.4476 |  |  | 32 | 4 mm
Y2 | Penolong Pendafar -1 | Hisense AN10DBG2 (1HP) | 1 | 850 | 850 | 1 | 850 |  | 4347.8261 |  | 32 | 4 mm
B2 | Bilik Tetamu | Hisense AN20DBG (2HP) | 1 | 1780 | 1780 | 1 | 1780 |  |  | 9104.8593 | 32 | 4 mm
R3 | Bilik Rundingan-1 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 | 5575.4476 |  |  | 32 | 4 mm
Y3 | Bilik Mesyurat(1) | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4 mm
B3 | Bilik Mesyurat(2) | Hisense AN10DBG2 (1HP) | 1 | 850 | 850 | 1 | 850 |  |  | 4347.8261 | 32 | 4 mm
R4 | Penolong Pendafar -2 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 | 5575.4476 |  |  | 32 | 4 mm
Y4 | Bilik Rundingan-2 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4 mm
B4 | Bilik Rundingan-3 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  |  | 5575.4476 | 32 | 4 mm
R5 | Bilik Rundingan-4 | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 | 5575.4476 |  |  | 32 | 4 mm
Y5 | Pusat Kejuruuteraan (1) | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4 mm
B5 | Pusat Kejuruuteraan (2) | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  |  | 5575.4476 | 32 | 4 mm
R6 | Pusat Kejuruuteraan (3) | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 | 5575.4476 |  |  | 32 | 4 mm
Y6 | Pusat Kejuruuteraan (4) | Hisense AN13DBG1 (1.5HP) | 1 | 1090 | 1090 | 1 | 1090 |  | 5575.4476 |  | 32 | 4 mm
TOTAL |  |  | 17 | 19380 | 19380 |  | 19380 | 33452.6854 | 32225.0639 | 33452.6854

## 2ND FLOOR - TCL LAMPU KOSON
GREEN BULIDING
2ND FLOOR & ROOF
Circuit No. | Descriptions |  | QTY | Connected | Total Connected | Diversity | Maximun | Rated Current | Rated Current | Rated Current | MCB | Cable Size
| Locations | Lamp type |  | Loads (W) | Loads (W) | Factor | Demand(W) | (mA) (Red) | (mA) (Yellow) | (mA) (Blue) | Rating (A SPN) | Size
R1 | Timblan Pengarah | Fluorescent 2 x 36W+Ballast 6 W | 4 | 84 | 336 | 0.8 | 268.8 | 1374.9361 |  |  | 6 | 1.5 mm
| Bilik Server | Fluorescent 1 x 36W+Ballast 6 W | 3 | 42 | 126 | 0.8 | 100.8 | 515.601 |  |  |  | 1.5 mm
| Bilik Setor | Fluorescent 1 x 36W+Ballast 6 W | 3 | 42 | 126 | 0.8 | 100.8 | 515.601 |  |  |  | 1.5 mm
[5 empty] | 0 | 0.8
Y1 | Bilik Pantri | Fluorescent 1 x 36W+Ballast 6 W | 2 | 42 | 84 | 0.8 | 67.2 |  | 343.734 |  | 6 | 1.5 mm
| Bilik Bincang | Fluorescent 2 x 36W+Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  |  | 1.5 mm
[5 empty] | 0 | 0.8
B1 | Bilik Pengarah | Fluorescent 2 x 36W+Ballast 6 W | 5 | 84 | 420 | 0.8 | 336 |  |  | 1718.6701 | 6 | 1.5 mm
| Bilik Tetamu | Fluorescent 2 x 36W+Ballast 6 W | 5 | 84 | 420 | 0.8 | 336 |  |  | 1718.6701 |  | 1.5 mm
[5 empty] | 0 | 0.8
R2 | Penolong Pendafar | Fluorescent 2 x 36W+Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 | 1031.202 |  |  | 6 | 1.5 mm
| Penolong Pendafar | Fluorescent 2 x 36W+Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 | 1031.202 |  |  |  | 1.5 mm
[5 empty] | 0 | 0.8
Y2 | Bilik Mesyurat | Fluorescent 2 x 36W+Ballast 6 W | 6 | 84 | 504 | 0.8 | 403.2 |  | 2062.4041 |  | 6 | 1.5 mm
B2 | Tandas | Fluorescent 1 x 36W+Ballast 6 W | 8 | 42 | 336 | 0.8 | 268.8 |  |  | 1374.9361 | 6 | 1.5 mm
[5 empty] | 0 | 0.8
R3 | R. Tangga/ Legar | Fluorescent 1 x 36W+Ballast 6 W | 2 | 42 | 84 | 0.8 | 67.2 | 343.734 |  |  | 6 | 1.5 mm
| Bikil Setor | Fluorescent 1 x 36W+Ballast 6 W | 3 | 42 | 126 | 0.8 | 100.8 | 515.601 |  |  |  | 1.5 mm
Y3 | Bilik Rundingan-1 | Fluorescent 2 x 36W+Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  | 6 | 1.5 mm
| Bilik Rundingan-1 | Fluorescent 2 x 36W+Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  |  | 1.5 mm
| Bilik Rundingan-1 | Fluorescent 2 x 36W+Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 |  | 1031.202 |  |  | 1.5 mm
B3 | Pusat Kejuruuteraan -1 | Fluorescent 2 x 36W+Ballast 6 W | 8 | 84 | 672 | 0.8 | 537.6 |  |  | 2749.8721 | 6 | 1.5 mm
R4 | Koridor | Fluorescent 1 x 36W+Ballast 6 W | 9 | 42 | 378 | 0.8 | 302.4 | 1546.8031 |  |  | 6 | 1.5 mm
Y4 | Pusat Kejuruuteraan -1 | Fluorescent 2 x 36W+Ballast 6 W | 8 | 84 | 672 | 0.8 | 537.6 |  | 2749.8721 |  | 6 | 1.5 mm
B4 | Bilik Rundingan-4 | Fluorescent 2 x 36W+Ballast 6 W | 3 | 84 | 252 | 0.8 | 201.6 |  |  | 1031.202 | 6 | 1.5 mm
R5 | TANDAS FAN | Ceiling Mounted Ventilating Fans | 6 | 25.7 | 154.2 | 0.8 | 123.36 | 630.9974 |  |  | 6 | 1.5 mm
| EMERGENCY | VEL 330/ST 1X1.2W | 3 | 1.2 | 3.6 | 0.8 | 2.88 | 14.7315 |  |  |  | 1.5 mm
Y5 | EMERGENCY | VEL 330/ST 1X1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 |  | 49.1049 |  | 6 | 1.5 mm
B5 | EMERGENCY | VEL 330/ST 1X1.2W | 10 | 1.2 | 12 | 0.8 | 9.6 |  |  | 49.1049 | 6 | 1.5 mm
R6 | EXIT SIGN CEILING | VSK 570/WP/RM 1X2.5W | 8 | 2.5 | 20 | 0.8 | 16 | 81.8414 |  |  | 6 | 1.5 mm
[5 empty] | 0 | 0.8
Y6 | EXIT SIGN CEILING | VSK 570/WP/RM 1X2.5W | 10 | 2.5 | 25 | 0.8 | 20 |  | 102.3018 |  | 6 | 1.5 mm
B6 | CELLING FAN | REGULATOR FANS 1X54W | 3 | 25.7 | 154.2 | 0.8 | 123.36 |  |  | 630.9974 | 6 | 1.5 mm
| EMERGENCY - ROOF | CEILING MOUNTED 1X1.2W | 2 | 2.5 | 5 | 0.8 | 4
R7 | EXIT SIGN - ROOF | KELUAR' SIGN 1X2.5W | 1 | 1.2 | 1.2 | 0.8 | 0.96 | 4.9105 |  |  | 6 | 1.5 mm
| ROOF - WALL MOUNTED | Fluorescent 1 x 36W+Ballast 6 W | 5 | 42 | 210 | 0.8 | 168 | 859.335
| ROOF - CEILING MOUNTED | Fluorescent 1 x 36W+Ballast 6 W | 4 | 42 | 168 | 0.8 | 134.4 | 687.468
TOTAL |  |  | 149 | 1533.7 | 6813.2 |  | 5450.56 | 9153.9642 | 9432.2251 | 9273.4527

## 2ND FLOOR - AC CALCULATION
GREEN BULIDING
2ND FLOOR
Room (BM) | Area (m²) | Heat Factor | Area (ft²) | Calculated HP | Final AC Selection | Qty AC | Remarks
Timblan Pengarah | 19.8204 | 60 | 213.3468 | 1.3475 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
Bilik Server | 19.8204 | 60 | 213.3468 | 1.3475 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
Bilik Setor | 20.44 | 60 | 220.0162 | 1.3896 | Ceiling Fan | - | No AC required
Bilik Pantri | 12 | 60 | 129.168 | 0.8158 | Ceiling Fan | - | No AC required
Bilik Bincang | 15.4 | 70 | 165.7656 | 1.2214 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
Bilik Pengarah | 23.92 | 60 | 257.4749 | 1.6262 | 2 HP | 1 | Hisense AN20DBG (2HP)
Bilik Tetamu | 23.92 | 70 | 257.4749 | 1.8972 | 2 HP | 1 | Hisense AN20DBG (2HP)
Penolong Pendafar | 13.08 | 60 | 140.7931 | 0.88922 | 1 HP | 1 | Hisense AN10DBG2 (1HP)
Penolong Pendafar | 13.08 | 60 | 140.7931 | 0.88922 | 1 HP | 1 | Hisense AN10DBG2 (1HP)
Bilik Mesyurat | 30.26 | 70 | 325.7186 | 2.4 | 2*1.5 HP | 2 | Hisense AN13DBG1 (1.5HP)
Tandas | 46.035 | 60 | 495.5207 | 3.1296 | Exhaust Fan | - | No AC required
R. Tangga/ Legar | 22.275 | 60 | 239.7681 | 1.5143 | - | - | No AC required
Bikil Setor | 11.54 | 60 | 124.2166 | 0.78453 | Ceiling Fan | - | No AC required
Bilik Rundingan-1 | 12.8284 | 70 | 138.0846 | 1.0175 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
Bilik Rundingan-2 | 14.5766 | 70 | 156.9028 | 1.1561 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
Bikil Rundingan-3 | 13.92 | 70 | 149.8349 | 1.104 | 1.5 HP | 2 | Hisense AN13DBG1 (1.5HP)
Bikil Rundingan-4 | 13.92 | 70 | 149.8349 | 1.104 | 1.5 HP | 1 | Hisense AN13DBG1 (1.5HP)
Pusat Kejuruuteraan | 75.4608 | 70 | 812.2601 | 5.9851 | 4*1.5 Hp | 4 | Hisense AN13DBG1 (1.5HP)

## SSB & MSB GREEN BUILDING
GREEM BUILDING
GREEN GROUND FLOOR | TCL (W) | MD (W)
DB (LIGHT&FAN) | 9255.5 | 7404.4
DB (AC) | 26088 | 26088
DB (POWER) | 26400 | 10560 | I SSB Ground | MD + 30% (W)
SSB | 61743.5 | 44052.4 | 100A | 97.2464
GREEN 1ST FLOOR | TCL (W) | MD (W)
DB (LIGHT&FAN) | 6326.2 | 5060.96
DB (AC) | 26088 | 26088
DB (POWER) | 21000 | 8400 | I SSB 1ST FLOOR | MD + 30% (W)
SSB | 53414.2 | 39548.96 | 100A | 87.305
GREEN 2ND FLOOR & ROOF | TCL (W) | MD (W)
DB (LIGHT&FAN) | 6813.2 | 5450.56
DB (POWER) | 30750 | 12300
DB (AC) | 19380 | 19380 | I SSB 2ND FLOOR & ROOF | MD + 30% (W)
SSB | 56943.2 | 37130.56 | 100A | 81.9663
MSB | TCL (W) | MD (W)
GREEM BUILDING | 172100.9 | 120731.92