## GREEN - G FLOOR
Quatity Lamp Calculation
No | Location (ENGLISH) | Location (MALAY) | Length | Width | Mounting Height | Area (L xW) | Room Index | CoU | Avg Illuminance | MF | Installed Lux | Lamp Code | Lamp Type | Lighting Design | Actual Lamp | Quantity Lamp | SHR MAX | SPACE | S/2
|  |  | L (m) | W (m) | hm (m) | A (m2) | K |  | Lux |  | CoU x MF |  |  | Lumen,LDL | Quantity | Used
1 | Server Room | BILIK SERVER | 4.98 | 4 | 3.1 | 19.92 | 0.71557 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 3.5913 | 4 | 1.25 | 3.875 | 1.9375
2 | Deputy Dean Office | TIMBALAN DEKAN | 4.98 | 4 | 3.1 | 19.92 | 0.71557 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 3.5913 | 4 | 1.25 | 3.875 | 1.9375
3 | Dean Office | BILIK DEKAN | 6 | 4 | 3.1 | 24 | 0.77419 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 4.3269 | 6 | 1.25 | 3.875 | 1.9375
4 | Printing Room | BILIK CETAK | 6.93 | 4 | 3.1 | 27.72 | 0.81811 | 0.38 | 300 | 0.8 | 0.304 | YBC 236 | FLUORESCENT 2×36W | 6500 | 4.2085 | 6 | 1.25 | 3.875 | 1.9375
5 | Store Room | BILIK SETOR | 5.05 | 4 | 3.8 | 20.2 | 0.58738 | 0.34 | 150 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 3.4276 | 4 | 1.25 | 4.75 | 2.375
6 | Assistant Registrar Office | PENOLONG DAFTAR | 3.98 | 3.25 | 3.1 | 12.935 | 0.57712 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 2.332 | 4 | 1.25 | 3.875 | 1.9375 | TOTAL LAMB
7 | Pantry Room 1 | BILIK PANTRI 1 | 3.98 | 3.27 | 3.1 | 13.0146 | 0.57907 | 0.34 | 300 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 4.4167 | 6 | 1.25 | 3.875 | 1.9375 | FLUORESCENT 2×36W | 70
8 | Assistant Registrar Office 2 | PENOLONG DAFTAR 2 | 3.98 | 3.25 | 3.1 | 12.935 | 0.57712 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 2.332 | 4 | 1.25 | 3.875 | 1.9375 | FLUORESCENT 1×36W | 58
9 | Guest Room | BILIK TETAMU | 3.98 | 3.27 | 3.1 | 13.0146 | 0.57907 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 2.3464 | 4 | 1.25 | 3.875 | 1.9375 | FLUORESCENT 1×18W | 12
10 | Meeting Room | BILIK MESYUARAT | 6 | 4 | 3.1 | 24 | 0.77419 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 4.3269 | 6 | 1.25 | 3.875 | 1.9375
11 | Switchboard Room (ER) | BILIK SWITCHBOARD (ER) | 2.65 | 2 | 3.8 | 5.3 | 0.29994 | 0.34 | 150 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.89932 | 1 | 1.25 | 4.75 | 2.375
12 | Store Room | BILIK SETOR | 3.045 | 2 | 3.8 | 6.09 | 0.31767 | 0.34 | 150 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.0334 | 2 | 1.25 | 4.75 | 2.375
13 | Meeting Room | BILIK MESYUARAT | 11.425 | 7 | 3.1 | 79.975 | 1.4002 | 0.46 | 300 | 0.8 | 0.368 | YBC 236 | FLUORESCENT 2×36W | 6500 | 10.0303 | 12 | 1.25 | 3.875 | 1.9375
14 | Staircase / Lobby | R. TANGGA / LEGAR | 12.15 | 4 | 3.8 | 48.6 | 0.79192 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 5.4977 | 6 | 1.25 | 4.75 | 2.375 | 70
15 | Utility Room | UTILITI | 7.425 | 3 | 3.8 | 22.275 | 0.56229 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 2.5198 | 4 | 1.25 | 4.75 | 2.375 | 58
16 | Engineering Center 1 | PUSAT KEJURUTERAAN 1 | 9.5 | 8 | 3.1 | 76 | 1.4009 | 0.46 | 300 | 0.8 | 0.368 | YBC 236 | FLUORESCENT 2×36W | 6500 | 9.5318 | 10 | 1.25 | 3.875 | 1.9375
17 | Engineering Center 2 | PUSAT KEJURUTERAAN 2 | 6.48 | 4 | 3.1 | 25.92 | 0.79783 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 4.6731 | 6 | 1.25 | 3.875 | 1.9375
18 | Male Toilet | TANDAS LELAKI | 4.98 | 3.75 | 3.8 | 18.675 | 0.56294 | 0.35 | 100 | 0.8 | 0.28 | YBC 118 | FLUORESCENT 1×18W | 1300 | 5.1305 | 6 | 1.25 | 4.75 | 2.375
19 | Female Toilet | TANDAS PEREMPUAN | 4.98 | 3.675 | 3.8 | 18.3015 | 0.55646 | 0.35 | 100 | 0.8 | 0.28 | YBC 118 | FLUORESCENT 1×18W | 1300 | 5.0279 | 6 | 1.25 | 4.75 | 2.375
20 | Female Prayer Room | SURAU (P) | 3.4 | 2.85 | 3.8 | 9.69 | 0.408 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 1.747 | 2 | 1.25 | 4.75 | 2.375
21 | Male Prayer Room | SURAU (L) | 4.2 | 2.075 | 3.8 | 8.715 | 0.36549 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 1.5712 | 2 | 1.25 | 4.75 | 2.375
22 | Pantry Room 2 | BILIK PANTRI 2 | 6 | 2.65 | 3.1 | 15.9 | 0.59295 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.7986 | 2 | 1.25 | 3.875 | 1.9375
23 | Car Porch Area | ANJUNG KERETA | 8.446 | 8.275 | 3.8 | 69.8906 | 1.1 | 0.45 | 50 | 0.8 | 0.36 | YBC 136 | FLUORESCENT 1×36W | 3250 | 2.9868 | 5 | 1.25 | 4.75 | 2.375
24 | Corridor A | CORRIDOR A | 9.2 | 1.125 | 2.6 | 10.35 | 0.38555 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.1708 | 2 | 1.25 | 3.25 | 1.625
25 | Corridor B | CORRIDOR B | 3.25 | 0.75 | 2.6 | 2.4375 | 0.23438 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.27574 | 1 | 1.25 | 3.25 | 1.625
26 | Corridor C | CORRIDOR C | 4 | 0.75 | 2.6 | 3 | 0.24291 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.33937 | 1 | 1.25 | 3.25 | 1.625
27 | Corridor D | CORRIDOR D | 12.825 | 1.125 | 2.6 | 14.4281 | 0.3978 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.6321 | 2 | 1.25 | 3.25 | 1.625
28 | Corridor E | CORRIDOR E | 3.125 | 1.125 | 2.6 | 3.5156 | 0.31816 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.3977 | 1 | 1.25 | 3.25 | 1.625
29 | Corridor F | CORRIDOR F | 3.725 | 1.125 | 2.6 | 4.1906 | 0.33233 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.47405 | 1 | 1.25 | 3.25 | 1.625
30 | Corridor G | CORRIDOR G | 4.625 | 1.225 | 2.6 | 5.6656 | 0.37249 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.64091 | 1 | 1.25 | 3.25 | 1.625
31 | Corridor H | CORRIDOR H | 6.55 | 1.35 | 2.6 | 8.8425 | 0.4305 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.0003 | 2 | 1.25 | 3.25 | 1.625
32 | Corridor J | CORRIDOR J | 8.275 | 1.275 | 2.6 | 10.5506 | 0.42491 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.1935 | 2 | 1.25 | 3.25 | 1.625
33 | Corridor K | CORRIDOR K | 21.275 | 1.15 | 2.6 | 24.4662 | 0.41963 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 2.7677 | 4 | 1.25 | 3.25 | 1.625
34 | Corridor L | CORRIDOR L | 8.55 | 1.35 | 2.6 | 11.5425 | 0.44843 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.3057 | 2 | 1.25 | 3.25 | 1.625
35 | Corridor M | CORRIDOR M | 4 | 1.15 | 2.6 | 4.6 | 0.34354 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.52036 | 1 | 1.25 | 3.25 | 1.625
36 | Corridor N | CORRIDOR N | 4.875 | 1.35 | 2.6 | 6.5813 | 0.40663 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.74449 | 1 | 1.25 | 3.25 | 1.625
37 | Corridor O | CORRIDOR O | 4.625 | 1.275 | 2.6 | 5.8969 | 0.38441 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.66707 | 1 | 1.25 | 3.25 | 1.625
38 | Corridor P | CORRIDOR P | 3.8 | 1.125 | 2.6 | 4.275 | 0.33385 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.4836 | 1 | 1.25 | 3.25 | 1.625
39 | Corridor Q | CORRIDOR Q | 3.125 | 1.125 | 2.6 | 3.5156 | 0.31816 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.3977 | 1 | 1.25 | 3.25 | 1.625
40 | Corridor R | CORRIDOR R | 12.825 | 1.125 | 2.6 | 14.4281 | 0.3978 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.6321 | 2 | 1.25 | 3.25 | 1.625
41 | Corridor S | CORRIDOR S | 4 | 0.75 | 2.6 | 3 | 0.24291 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.33937 | 1 | 1.25 | 3.25 | 1.625
42 | Corridor T | CORRIDOR T | 3.25 | 0.75 | 2.6 | 2.4375 | 0.23438 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 0.27574 | 1 | 1.25 | 3.25 | 1.625

## GREEN - 1ST FLOOR
Quatity Lamp Calculation
No | Location | Location | Length | Width | Mounting Height | Area (L xW) | Room Index | CoU | Avg Illuminance | MF | Installed Lux | Lamp Code | Lamp Type | Lighting Design | Quantity of | Actual Quantity | SHR MAX | SPACE | S/2
|  |  | L (m) | W (m) | hm (m) | A (m2) | K |  | Lux |  | CoU x MF |  |  | Lumen , LDL | Lamp Used | Lamp Used
1 | Server Room | Bilik Server | 5.15 | 4 | 3.8 | 20.6 | 0.59246 | 0.34 | 300 | 0.8 | 0.272 | YBC 236 | FLUORESCENT 2×36W | 6500 | 3.4955 | 4 | 1.25 | 4.75 | 2.375
2 | Assitant Dean | Timbalan Dekan | 4.89 | 3.89 | 3.1 | 19.0221 | 0.69888 | 0.34 | 300 | 0.8 | 0.272 | YBC 236 | FLUORESCENT 2×36W | 6500 | 3.2277 | 4 | 1.25 | 3.875 | 1.9375
3 | Dean Meeting | Mesyuarat Dekan | 3.89 | 5.93 | 3.1 | 23.0677 | 0.75776 | 0.34 | 300 | 0.8 | 0.272 | YBC 236 | FLUORESCENT 2×36W | 6500 | 3.9142 | 4 | 1.25 | 3.875 | 1.9375
4 | Dean Meeting | Dekan | 4 | 5.98 | 3.1 | 23.92 | 0.77316 | 0.34 | 300 | 0.8 | 0.272 | YBC 236 | FLUORESCENT 2×36W | 6500 | 4.0588 | 6 | 1.25 | 3.875 | 1.9375
5 | Guest Room | Tetamu | 4.98 | 2.95 | 3.1 | 14.691 | 0.59761 | 0.34 | 150 | 0.8 | 0.272 | YBC 236 | FLUORESCENT 2×36W | 6500 | 1.2464 | 2 | 1.25 | 3.875 | 1.9375
6 | Ass Registar | Penolong Daftar | 3.275 | 4 | 3.1 | 13.1 | 0.58087 | 0.34 | 200 | 0.8 | 0.272 | YBC 236 | FLUORESCENT 2×36W | 6500 | 1.4819 | 2 | 1.25 | 3.875 | 1.9375
7 | Cetak | Cetak | 2.275 | 4 | 3.1 | 9.1 | 0.46781 | 0.34 | 150 | 0.8 | 0.272 | YBC 236 | FLUORESCENT 2×36W | 6500 | 0.77206 | 1 | 1.25 | 3.875 | 1.9375
8 | Stor | Setor | 4 | 3.11 | 3.8 | 12.44 | 0.46043 | 0.34 | 200 | 0.8 | 0.272 | YBC 236 | FLUORESCENT 2×36W | 6500 | 1.4072 | 2 | 1.25 | 4.75 | 2.375
9 | Pusat 1 | Pusat 1 | 4 | 3.963 | 3.1 | 15.852 | 0.64216 | 0.34 | 300 | 0.8 | 0.272 | YBC 236 | FLUORESCENT 2×36W | 6500 | 2.6898 | 3 | 1.25 | 3.875 | 1.9375
10 | Engineering Area | Pusat Kejuruteraan | 15.12 | 12 | 3.1 | 181.44 | 2.1582 | 0.56 | 500 | 0.8 | 0.448 | YBC 236 | FLUORESCENT 2×36W | 6500 | 31.1538 | 32 | 1.25 | 3.875 | 1.9375
11 | Toilet (M) | Tandas (L) | 3.75 | 4.89 | 3.8 | 18.3375 | 0.55853 | 0.34 | 200 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 4.1488 | 5 | 1.25 | 4.75 | 2.375
12 | Toilet (F) | Tandas (P) | 3.75 | 4.89 | 3.8 | 18.3375 | 0.55853 | 0.34 | 200 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 4.1488 | 5 | 1.25 | 4.75 | 2.375
13 | Stairs | Tangga | 3 | 7.425 | 3.8 | 22.275 | 0.56229 | 0.34 | 300 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 7.5594 | 8 | 1.25 | 4.75 | 2.375
14 | Store Room | Bilik Setor | 2 | 5.75 | 3.8 | 11.5 | 0.39049 | 0.34 | 150 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.9514 | 2 | 1.25 | 4.75 | 2.375
15 | Coordination Centre | Pusat Penyelaras 1 | 4.275 | 3.52 | 3.1 | 15.048 | 0.62273 | 0.34 | 300 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 5.1068 | 4 | 1.25 | 3.875 | 1.9375
16 | Utility | Utiliti | 7 | 2.51 | 3.8 | 17.57 | 0.48619 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.9876 | 2 | 1.25 | 4.75 | 2.375
17 | Coordination Centre | Pusat Penyelaras 2 | 3.49 | 4.725 | 3.1 | 16.4902 | 0.64753 | 0.34 | 300 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 5.5962 | 6 | 1.25 | 3.875 | 1.9375
18 | Pusat 2 | Center | 3.49 | 4.725 | 3.8 | 16.4902 | 0.52825 | 0.34 | 200 | 0.8 | 0.272 | YBC 236 | FLUORESCENT 2×36W | 6500 | 3.7308 | 4 | 1.25 | 4.75 | 2.375
19 | Corridor | Korridor | 7 | 2.51 | 3.8 | 17.57 | 0.48619 | 0.34 | 150 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 2.9813 | 3 | 1.25 | 4.75 | 2.375
20 | Concrete Roof | Bumbung Konkrit | 7.12 | 7.05 | 3.8 | 50.196 | 0.93221 | 0.4 | 50 | 0.8 | 0.32 | YBC 136 | FLUORESCENT 1×36W | 3250 | 2.8391 | 3 | 1.25 | 4.75 | 2.375

## GREEN - 2ND FLOOR
Quatity Lamp Calculation
No | Location | Length | Width | Mounting Height | Area (L xW) | Room Index | CoU | Avg Illuminance | MF | Installed Lux | Lamp Code | Lamp Type | Lighting Design | Actual Lamp | Quantity Lamp | SHR MAX | SPACE | S/2
|  | L (m) | W (m) | hm (m) | A (m2) | K |  | Lux |  | CoU x MF |  |  | Lumen , LDL | Quantity | Used
1 | Timblan Pengarah | 4.98 | 3.98 | 3.1 | 19.8204 | 0.71358 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 3.5734 | 4 | 1.25 | 3.875 | 1.9375
2 | Bilik Server | 4.98 | 3.98 | 3.1 | 19.8204 | 0.71358 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 2.2421 | 3 | 1.25 | 3.875 | 1.9375
3 | Bilik Setor | 5.11 | 4 | 3.8 | 20.44 | 0.59044 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 2.3122 | 3 | 1.25 | 4.75 | 2.375
4 | Bilik Pantri | 4 | 3 | 3.1 | 12 | 0.553 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.3575 | 2 | 1.25 | 3.875 | 1.9375
5 | Bilik Bincang | 4 | 3.85 | 3.1 | 15.4 | 0.63283 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 2.7764 | 3 | 1.25 | 3.875 | 1.9375
6 | Bilik Pengarah | 5.98 | 4 | 3.1 | 23.92 | 0.77316 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 4.3125 | 5 | 1.25 | 3.875 | 1.9375
7 | Bilik Tetamu | 5.98 | 4 | 3.1 | 23.92 | 0.77316 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 4.3125 | 5 | 1.25 | 3.875 | 1.9375
8 | Penolong Pendafar | 4 | 3.27 | 3.1 | 13.08 | 0.58038 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 2.3582 | 3 | 1.25 | 3.875 | 1.9375
9 | Penolong Pendafar | 4 | 3.27 | 3.1 | 13.08 | 0.58038 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 5308 | 2.8877 | 3 | 1.25 | 3.875 | 1.9375
10 | Bilik Mesyurat | 7.565 | 4 | 3.1 | 30.26 | 0.84404 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 5.4555 | 6 | 1.25 | 3.875 | 1.9375
11 | Tandas | 7.425 | 6.2 | 3.8 | 46.035 | 0.88914 | 0.4 | 100 | 0.8 | 0.32 | YBC 136 | FLUORESCENT 1×36W | 3250 | 4.4264 | 8 | 1.25 | 4.75 | 2.375
12 | R. Tangga/ Legar | 7.425 | 3 | 3.8 | 22.275 | 0.56229 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 2.5198 | 3 | 1.25 | 4.75 | 2.375
13 | Bikil Setor | 5.77 | 2 | 3.8 | 11.54 | 0.39084 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1×36W | 3250 | 1.3054 | 2 | 1.25 | 4.75 | 2.375
14 | Bilik Rundingan-1 | 4.725 | 2.715 | 3.1 | 12.8284 | 0.55621 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 2.3128 | 3 | 1.25 | 3.875 | 1.9375
15 | Bilik Rundingan-2 | 4.725 | 3.085 | 3.1 | 14.5766 | 0.60207 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 2.628 | 3 | 1.25 | 3.875 | 1.9375
16 | Bikil Rundingan-3 | 4 | 3.48 | 3.1 | 13.92 | 0.60031 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 2.5096 | 3 | 1.25 | 3.875 | 1.9375
17 | Bikil Rundingan-4 | 4 | 3.48 | 3.1 | 13.92 | 0.60031 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2×36W | 6500 | 2.5096 | 3 | 1.25 | 3.875 | 1.9375
18 | Pusat Kejuruuteraan | 9.48 | 7.96 | 3.1 | 75.4608 | 1.3958 | 0.46 | 300 | 0.8 | 0.368 | YBC 236 | FLUORESCENT 2×36W | 6500 | 9.4641 | 16 | 1.25 | 3.875 | 1.9375
19 | Koridor | 18.5 | 3.96 | 3.8 | 73.26 | 0.85837 | 0.4 | 100 | 0.8 | 0.32 | YBC 136 | FLUORESCENT 1×36W | 3250 | 7.0442 | 9 | 1.25 | 4.75 | 2.375

## HEPA - 1ST FLOOR
Quatity Lamp Calculation
No | Location | Length | Width | Mounting Height | Area (L xW) | Room Index | CoU | Avg Illuminance | MF | Installed Lux | Lamp Code | Lamp Type | Lighting Design | Actual Lamp | Quantity Lamp | SHR MAX | SPACE | S/2
|  | L (m) | W (m) | hm (m) | A (m2) | K |  | Lux |  | CoU x MF |  |  | Lumen , LDL | Quantity | Used
1 | RUANG KERJA 1 | 3.8 | 2.9 | 3.1 | 11.02 | 0.53057 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 1.9868 | 2 | 1.25 | 3.875 | 1.9375
2 | RUANG KERJA 2 | 6.05 | 4.3 | 3.1 | 26.015 | 0.81082 | 0.38 | 300 | 0.8 | 0.304 | YBC 236 | FLUORESCENT 2X36W | 6500 | 3.9496 | 4 | 1.25 | 3.875 | 1.9375
3 | RUANG KERJA 3 | 4.5 | 3.4 | 3.1 | 15.3 | 0.62474 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.7584 | 3 | 1.25 | 3.875 | 1.9375
4 | RUANG KERJA 4 | 4.5 | 2.5 | 3.1 | 11.25 | 0.51843 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.0282 | 3 | 1.25 | 3.875 | 1.9375
5 | RUANG KERJA 5 | 4.5 | 3.02 | 3.1 | 13.59 | 0.58296 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4501 | 3 | 1.25 | 3.875 | 1.9375
6 | RUANG KERJA 6 | 4.5 | 3 | 3.1 | 13.5 | 0.58065 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4339 | 3 | 1.25 | 3.875 | 1.9375
7 | RUANG KERJA 7 | 4.5 | 3.3 | 3.1 | 14.85 | 0.61414 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.6773 | 3 | 1.25 | 3.875 | 1.9375
8 | RUANG KERJA 8 | 4.5 | 3.02 | 3.1 | 13.59 | 0.58296 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4501 | 3 | 1.25 | 3.875 | 1.9375
9 | RUANG KERJA 9 | 4.5 | 3 | 3.1 | 13.5 | 0.58065 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4339 | 3 | 1.25 | 3.875 | 1.9375
10 | BILIK FAIL | 4.5 | 4.5 | 3.1 | 20.25 | 0.72581 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 3.6508 | 4 | 1.25 | 3.875 | 1.9375
11 | BILIK CETAK | 4.5 | 4.5 | 3.1 | 20.25 | 0.72581 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 3.6508 | 4 | 1.25 | 3.875 | 1.9375 | 94 | 1X36
12 | LALUAN 1 | 22.5 | 1.6 | 2.6 | 36 | 0.57453 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 4.0724 | 8 | 1.25 | 3.25 | 1.625
13 | LALUAN 1.1 | 2.9 | 2.4 | 2.6 | 6.96 | 0.50508 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 0.78733 | 1 | 1.25 | 3.25 | 1.625 | 103 | 2X36
14 | LALUAN 1.2 | 4.5 | 2.5 | 2.6 | 11.25 | 0.61813 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.2726 | 2 | 1.25 | 3.25 | 1.625
15 | TANDAS | 6.3 | 6.07 | 3.8 | 38.241 | 0.81353 | 0.4 | 100 | 0.8 | 0.32 | YBC 136 | FLUORESCENT 1X36W | 3250 | 3.677 | 11 | 1.25 | 4.75 | 2.375
16 | TANGGA 3 | 5.1 | 3 | 3.8 | 15.3 | 0.49708 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.7308 | 3 | 1.25 | 4.75 | 2.375
17 | FOYER 2 | 6.3 | 2.3 | 2.6 | 14.49 | 0.64803 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.6391 | 2 | 1.25 | 3.25 | 1.625
18 | BILIK ALAT MUZIK 1 | 8.8 | 4.5 | 3.1 | 39.6 | 0.96047 | 0.38 | 200 | 0.8 | 0.304 | YBC 236 | FLUORESCENT 2X36W | 6500 | 4.0081 | 6 | 1.25 | 3.875 | 1.9375
19 | BILIK ALAT MUZIK 2 | 8.8 | 4.4 | 3.1 | 38.72 | 0.94624 | 0.38 | 200 | 0.8 | 0.304 | YBC 236 | FLUORESCENT 2X36W | 6500 | 3.919 | 6 | 1.25 | 3.875 | 1.9375
20 | BILIK KEBUDAYAAN | 8.9 | 8.8 | 3.1 | 78.32 | 1.4274 | 0.46 | 200 | 0.8 | 0.368 | YBC 236 | FLUORESCENT 2X36W | 6500 | 6.5485 | 9 | 1.25 | 3.875 | 1.9375
21 | BILIK KOSTUM PAKAIAN | 8.8 | 6 | 3.8 | 52.8 | 0.93883 | 0.38 | 150 | 0.8 | 0.304 | YBC 236 | FLUORESCENT 2X36W | 6500 | 4.0081 | 6 | 1.25 | 4.75 | 2.375
22 | LALUAN 2 | 23.07 | 1.8 | 2.6 | 41.526 | 0.6422 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 4.6975 | 8 | 1.25 | 3.25 | 1.625
23 | TANGGA 1 | 5.2 | 3.2 | 3.8 | 16.64 | 0.5213 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.8824 | 3 | 1.25 | 4.75 | 2.375
24 | LALUAN 2.1 | 2.1 | 1.2 | 2.6 | 2.52 | 0.29371 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 0.28507 | 1 | 1.25 | 3.25 | 1.625
25 | BILIK SOLAT LELAKI | 6.3 | 3.07 | 3.8 | 19.341 | 0.54319 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 3.487 | 4 | 1.25 | 4.75 | 2.375
26 | BILIK SOLAT PEREMPUAN | 6.3 | 3 | 3.8 | 18.9 | 0.5348 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 3.4075 | 4 | 1.25 | 4.75 | 2.375
27 | BILIK PERALATAN PELAJAR | 10.6 | 4.5 | 3.1 | 47.7 | 1.019 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 8.5998 | 9 | 1.25 | 3.875 | 1.9375
28 | KAUNTER LAYAN PELAJAR | 4.5 | 4.3 | 3.1 | 19.35 | 0.70931 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 3.4886 | 4 | 1.25 | 3.875 | 1.9375
29 | RUANG KERJA 10 | 4.5 | 3.1 | 3.1 | 13.95 | 0.59211 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.515 | 3 | 1.25 | 3.875 | 1.9375
30 | RUANG KERJA 11 | 4.5 | 3.02 | 3.1 | 13.59 | 0.58296 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4501 | 3 | 1.25 | 3.875 | 1.9375
31 | BILIK RUNDINGAN PELAJAR 2 | 4.5 | 3.2 | 3.1 | 14.4 | 0.60327 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.5962 | 3 | 1.25 | 3.875 | 1.9375
32 | BILIK RUNDINGAN PELAJAR 1 | 4.5 | 3.05 | 3.1 | 13.725 | 0.58641 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4745 | 3 | 1.25 | 3.875 | 1.9375
33 | PEJABAT AM | 4.5 | 6 | 3.1 | 27 | 0.82949 | 0.38 | 300 | 0.8 | 0.304 | YBC 236 | FLUORESCENT 2X36W | 6500 | 4.0992 | 6 | 1.25 | 3.875 | 1.9375
34 | RUANG MENUNGGU PELAJAR | 4.5 | 6 | 2.6 | 27 | 0.98901 | 0.4 | 100 | 0.8 | 0.32 | YBC 136 | FLUORESCENT 1X36W | 3250 | 2.5962 | 4 | 1.25 | 3.25 | 1.625
35 | TANGGA 2 | 5.1 | 3 | 3.8 | 15.3 | 0.49708 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.7308 | 3 | 1.25 | 4.75 | 2.375
36 | FOYER 1 | 6.1 | 2.3 | 2.6 | 14.03 | 0.6424 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.5871 | 3 | 1.25 | 3.25 | 1.625
37 | ELEKTRIK | 4.5 | 3 | 3.8 | 13.5 | 0.47368 | 0.34 | 150 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 2.2907 | 3 | 1.25 | 4.75 | 2.375
38 | TELEFON&ICT | 3.4 | 1.5 | 3.1 | 5.1 | 0.33575 | 0.32 | 500 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 1.5325 | 2 | 1.25 | 3.875 | 1.9375
39 | LALUAN 3 | 10.5 | 1.6 | 2.6 | 16.8 | 0.53401 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.9005 | 4 | 1.25 | 3.25 | 1.625
40 | LALUAN 4 | 10.6 | 1.3 | 2.6 | 13.78 | 0.44538 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.5588 | 4 | 1.25 | 3.25 | 1.625
41 | ANJUNG KERETA | 6.4 | 6 | 3.8 | 38.4 | 0.81494 | 0.4 | 30 | 0.8 | 0.32 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.1077 | 2 | 1.25 | 4.75 | 2.375
42 | LALUAN 5 | 9.1 | 1.1 | 2.6 | 10.01 | 0.37745 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.1324 | 3 | 1.25 | 3.25 | 1.625
43 | LALUAN 5.1 | 6.07 | 2.8 | 2.6 | 16.996 | 0.73697 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.9226 | 2 | 1.25 | 3.25 | 1.625
44 | LALUAN 6 | 31.2 | 2.3 | 2.6 | 71.76 | 0.82388 | 0.4 | 100 | 0.8 | 0.32 | YBC 136 | FLUORESCENT 1X36W | 3250 | 6.9 | 10 | 1.25 | 3.25 | 1.625
45 | LALUAN 6.1 | 7.3 | 1.4 | 2.6 | 10.22 | 0.45181 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.1561 | 3 | 1.25 | 3.25 | 1.625
46 | LALUAN 6.2 | 4.7 | 2.02 | 2.6 | 9.494 | 0.54338 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.074 | 2 | 1.25 | 3.25 | 1.625
47 | LALUAN 6.3 | 31.2 | 1.9 | 2.6 | 59.28 | 0.68882 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 6.7059 | 10 | 1.25 | 3.25 | 1.625
48 | LALUAN 6.4 | 6.3 | 1.5 | 2.6 | 9.45 | 0.46598 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.069 | 2 | 1.25 | 3.25 | 1.625

## HEPA 2ND FLOOR
Quatity Lamp Calculation
No | Location | Length | Width | Mounting Height | Area (L xW) | Room Index | CoU | Avg Illuminance | MF | Installed Lux | Lamp Code | Lamp Type | Lighting Design | Actual Lamp | Quantity Lamp | SHR MAX | SPACE | S/2
|  | L (m) | W (m) | hm (m) | A (m2) | K |  | Lux |  | CoU x MF |  |  | Lumen , LDL | Quantity | Used
1 | TANGGA 2 | 5.15 | 3 | 3.8 | 15.45 | 0.49887 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.7477 | 3 | 1.25 | 4.75 | 2.375
2 | PEJABAT AM | 9 | 6 | 3.1 | 54 | 1.1613 | 0.42 | 300 | 0.8 | 0.336 | YBC 236 | FLUORESCENT 2X36W | 6500 | 7.4176 | 8 | 1.25 | 3.875 | 1.9375
3 | L+C7:T10 A L U A N 2.1 | 6.3 | 1.5 | 2.6 | 9.45 | 0.46598 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.069 | 2 | 1.25 | 3.25 | 1.625
4 | LALUAN 2.2 | 3.76 | 6 | 2.6 | 22.56 | 0.88903 | 0.4 | 100 | 0.8 | 0.32 | YBC 136 | FLUORESCENT 1X36W | 3250 | 2.1692 | 4 | 1.25 | 3.25 | 1.625
5 | L A L U A N 2.3 | 16.8 | 2.1 | 2.6 | 35.28 | 0.71795 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 3.991 | 6 | 1.25 | 3.25 | 1.625
6 | L A L U A N 2.4 | 16.8 | 1.6 | 2.6 | 26.88 | 0.56187 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 3.0407 | 4 | 1.25 | 3.25 | 1.625
7 | BILIK PEGAWAI 3 | 6 | 4.5 | 3.1 | 27 | 0.82949 | 0.38 | 300 | 0.8 | 0.304 | YBC 236 | FLUORESCENT 2X36W | 6500 | 4.0992 | 5 | 1.25 | 3.875 | 1.9375
8 | RUANG KERJA 20 | 4.55 | 3 | 3.1 | 13.65 | 0.58321 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4609 | 3 | 1.25 | 3.875 | 1.9375
9 | RUANG KERJA 21 | 4.55 | 3 | 3.1 | 13.65 | 0.58321 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4609 | 3 | 1.25 | 3.875 | 1.9375 |  | TOTAL LAMB
10 | BILIK ALAT TULIS | 4.55 | 1.5 | 3.1 | 6.825 | 0.3639 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 1.2305 | 2 | 1.25 | 3.875 | 1.9375 | FLUORESCENT 1X36W | 61
11 | RISER ICT+ELEKTRIK | 4.5 | 3 | 3.1 | 13.5 | 0.58065 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4339 | 3 | 1.25 | 3.875 | 1.9375 | FLUORESCENT 2X36W | 76
12 | RUANG KERJA 16 | 6 | 4.5 | 3.1 | 27 | 0.82949 | 0.38 | 300 | 0.8 | 0.304 | YBC 236 | FLUORESCENT 2X36W | 6500 | 4.0992 | 5 | 1.25 | 3.875 | 1.9375
13 | RUANG KERJA 17 | 3 | 4.5 | 3.1 | 13.5 | 0.58065 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4339 | 3 | 1.25 | 3.875 | 1.9375
14 | RUANG KERJA 18 | 3 | 4.5 | 3.1 | 13.5 | 0.58065 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4339 | 3 | 1.25 | 3.875 | 1.9375
15 | RUANG KERJA 19 | 4.45 | 4.5 | 3.1 | 20.025 | 0.72175 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 3.6103 | 4 | 1.25 | 3.875 | 1.9375
16 | BILIK RANGKAIAN ICT+PANTRI | 6.1 | 5.1 | 3.8 | 31.11 | 0.73097 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 5.6088 | 6 | 1.25 | 4.75 | 2.375
17 | L A L U A N 2.5 | 4.3 | 1.3 | 2.6 | 5.59 | 0.38393 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 0.63235 | 1 | 1.25 | 3.25 | 1.625
18 | L A L U A N 2.6 | 11.7 | 1.9 | 2.6 | 22.23 | 0.62868 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 2.5147 | 4 | 1.25 | 3.25 | 1.625
19 | TANGGA 1 | 5 | 3.3 | 3.8 | 16.5 | 0.52315 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.8665 | 3 | 1.25 | 4.75 | 2.375
20 | L A L U A N 2.7 | 4.28 | 1.36 | 2.6 | 5.8208 | 0.39694 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 0.65846 | 2 | 1.25 | 3.25 | 1.625
21 | TANDAS(P)(L)+SERVIS | 6.1 | 5 | 3.1 | 30.5 | 0.88637 | 0.4 | 100 | 0.8 | 0.32 | YBC 136 | FLUORESCENT 1X36W | 3250 | 2.9327 | 8 | 1.25 | 3.875 | 1.9375
22 | TANGGA 3 | 5.15 | 3 | 3.8 | 15.45 | 0.49887 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.7477 | 3 | 1.25 | 4.75 | 2.375
23 | L A L U A N 2.8 | 5.1 | 1.8 | 2.6 | 9.18 | 0.51171 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.0385 | 2 | 1.25 | 3.25 | 1.625
24 | LALUAN 2.9 | 6.1 | 3.8 | 2.6 | 23.18 | 0.90054 | 0.4 | 100 | 0.8 | 0.32 | YBC 136 | FLUORESCENT 1X36W | 3250 | 2.2288 | 4 | 1.25 | 3.25 | 1.625
25 | L A L U A N 2.1.1 | 6.4 | 1.4 | 2.6 | 8.96 | 0.44181 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.0136 | 2 | 1.25 | 3.25 | 1.625
26 | L A L U A N 2.1.2 | 15.1 | 1.6 | 2.6 | 24.16 | 0.55643 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 2.733 | 5 | 1.25 | 3.25 | 1.625
27 | L A L U A N 2.1.3 | 16.6 | 2.1 | 2.6 | 34.86 | 0.71699 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 3.9434 | 6 | 1.25 | 3.25 | 1.625
28 | RUANG MENUNGGU | 6.1 | 2.8 | 2.6 | 17.08 | 0.73812 | 0.34 | 100 | 0.8 | 0.272 | YBC 136 | FLUORESCENT 1X36W | 3250 | 1.9321 | 2 | 1.25 | 3.25 | 1.625
29 | RUANG KERJA 12 | 3.1 | 4.5 | 3.1 | 13.95 | 0.59211 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.515 | 3 | 1.25 | 3.875 | 1.9375
30 | RUANG KERJA 13 | 3.1 | 4.5 | 3.1 | 13.95 | 0.59211 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.515 | 3 | 1.25 | 3.875 | 1.9375
31 | RUANG KERJA 14 | 4.5 | 3.03 | 3.1 | 13.635 | 0.58412 | 0.32 | 300 | 0.8 | 0.256 | YBC 236 | FLUORESCENT 2X36W | 6500 | 2.4582 | 3 | 1.25 | 3.875 | 1.9375
32 | BILIK PEGAWAI 1 | 9 | 4.5 | 3.1 | 40.5 | 0.96774 | 0.38 | 300 | 0.8 | 0.304 | YBC 236 | FLUORESCENT 2X36W | 6500 | 6.1488 | 7 | 1.25 | 3.875 | 1.9375
33 | BILIK PEGAWAI 2 | 6 | 4.5 | 3.1 | 27 | 0.82949 | 0.38 | 300 | 0.8 | 0.304 | YBC 236 | FLUORESCENT 2X36W | 6500 | 4.0992 | 5 | 1.25 | 3.875 | 1.9375
34 | BILIK MESYUARAT UTAMA | 10.6 | 7.5 | 3.1 | 79.5 | 1.4169 | 0.46 | 300 | 0.8 | 0.368 | YBC 236 | FLUORESCENT 2X36W | 6500 | 9.9707 | 10 | 1.25 | 3.875 | 1.9375